LIGO Laboratory / LIGO Scientific Collaboration

LIGO-T1100046-v2	LIGO	03/01/11

aLIGO DC Power System Design

D.Kinzel

Distribution of this document:

LIGO Scientific Collaboration

This is an internal working note

of the LIGO Laboratory.

| California Institute of Technology LIGO Project – MS 18-34 1200 E. California Blvd. Pasadena, CA 91125 Phone (626) 395-2129 Fax (626) 304-9834 E-mail: info@ligo.caltech.edu | Massachusetts Institute of Technology LIGO Project – NW22-295 185 Albany St Cambridge, MA 02139 Phone (617) 253-4824 Fax (617) 253-7014 E-mail: info@ligo.mit.edu |
| --- | --- |
| LIGO Hanford Observatory P.O. Box 1970 Mail Stop S9-02 Richland WA 99352 Phone 509-372-8106 Fax 509-372-8137 | LIGO Livingston Observatory P.O. Box 940 Livingston, LA 70754 Phone 225-686-3100 Fax 225-686-7189 |

http://www.ligo.caltech.edu/

# Introduction

This document describes the design of the DC Power system that provides the DC power required to power Advanced LIGO (aLIGO) electronic racks.

# Scope

The scope of this document is to outline the design of the DC power distribution system required to support aLIGO electronic chassis.  Due to the existence of a variety of power requirements, the scope is limited to a known specific subset of DC power distribution components.  Outlying requirements are discussed briefly at the end.

This document is limited to discussing:

- Provision of two ubiquitous voltages, +/- 18VDC and +/- 24VDC, at 20A.

- Room layouts as related to DC power requirements

- Rack layouts as related to DC power requirements

- DC Power supplies

- DC Power strips (and the existing DC power box for high current usage)

- Cables that externally connect DC power supplies to electronics rack

Specifically not in the scope of this document are complete discussions of:

- Power to rooms not specified in the rooms list

- Power to racks not specified in the racks list

- Power supply requirements for voltages other than the four listed

- Cables that are internal to racks, i.e., from power strips to electronics chassis

# Overview

This design is concerned with:

- DC power supplies

- +/-18VDC power strips

- +/-24VDC power strips

- High current power boxes

- +24VDC power strips

6. Cabling between DC power supplies and DC power strips (and boxes)

For aLIGO installation, electronics racks are strategically positioned near chambers throughout the LVEA and end station VEAs to supply many of the necessary interconnects for control and monitoring of crucial functions of the interferometer.  (See (LIGO-D1003141 and LIGO-D1002704 for room layouts.)  Additional racks have been designed that are repositories of similar control and monitoring functions organized by subsystem but designed to be offloaded from the LVEA and VEAs into rooms designed for that purpose. (See LIGO-G1001032 for rack layouts.)

These racks often have similar requirements for the DC power that runs the electronics that they contain.  Electronic chassis for aLIGO have been designed to extensively use +/- 18VDC and +/- 24VDC.  (See LIGO-T1100047 for power supply requirements.)  Wiring conventions exist that include specifications for cable jacket colors, single conductor wiring insulation colors, and connector types. (See LIGO-T1100048 for these wiring conventions.)  In addition, the IO chassis specified by the DAQ subsystem are designed to use +24VDC exclusively.  These facts allow for a common method of providing these specific DC power requirements - DC power strips.  Such power strips have been designed and prototyped.

Each rack that requires one is provided a power strip (see LIGO-D1002189) that sources both positive and negative voltages for a specific voltage.  Two power strip variations have been designed: one for +/-18VDC and one for +/-24VDC.  These use different connectors to prevent accidental erroneous connections and cables with different colored jackets as visual indicators of their assigned potential.  Typically, a set of two DC power supplies needs to be provided for each such rack power strip.  These two power supplies share a common return connection.  Note that for IO chassis, only one power supply is required because there is no requirement for -24V.  However, due to power consumption, this one supply can only service up to four IO chassis.  (See LIGO-T1100049 for IO chassis power usage.)

In the case of the IO chassis, previous discussions have established the need for IO chassis to be powered from power supplies that are not also used to power electronics, for the purpose of being able to manage computer on/off functions separately from electronics on/off functions.  In addition, not all electronics racks require IO chassis.  Therefore each rack that requires one is to be provided with a +24V power strip that can be used to power up to four (4) IO chassis. (See LIGO-D1100034)

High current power boxes may be required for some applications.  These boxes provide up to 14 connections via bus bar methodology.  (See LIGO-D070124 for the high current box design.)

A list of the rack requirements for these power strips is below.  Note that this assessment is for the Livingston interferometer and when adjusted for all three IFOs, the estimated number of components must be 3 times as many.  Additional equipment will be required for the college laboratories.

# Design

The following figures provide an overview of the relationships between

- Rooms and types of rack they house

CER (CDS Electronics Room)				CPR (CDS Power Room)

Figure 1: CDS Electronics Room and CDS Power Room

- Subsystem electronics racks and DC power supply racks

Figure 2: Electronics Rack and DC Power Supply Rack

- DC power supplies and subsystem electronics racks

Figure 3: Each DC Power Supply Sources Only One Electronics Rack

- DC extension cables that interconnect DC power supplies and subsystem electronics racks

Figure 4: Standard DC Power Connecting Scheme

## Common Components

The DC power distribution system will use the following standard components.

- DC power supplies

- +/-18VDC power strips

- +/-24VDC power strips

- High current power boxes

- +24VDC power strips

- Cabling between DC power supplies and DC power strips (and boxes)

- Note that common DC extension cords have been designed and are preferred for interconnecting between the DC power strips and the electronics chassis.  Their specifications may be found in LIGO-D1002209.

## End Stations

At the end stations, similar rooms and racks have been determined and will use the same types of components.

# Equipment Lists

The following tables describe the DC power distribution components required for the current LLO L1 IFO configuration.

## Table 1: Power Supplies Required by Rack

Table 1 provides a list of power supplies required for the LLO DC Power distribution system. For LLO L1 there are a total of 102 18V supplies required, and 70 24V supplies.

| Power Rack Name | Position | Provides Power For | Electronics Rack Name | Voltage | Subsystem |
| --- | --- | --- | --- | --- | --- |
| L1-VDC-C1 | U01-A | IO Chassis | L1-SUS-C2 | +24 | SUS |
| L1-VDC-C1 | U01-B | IO Chassis | L1-SUS-C3 | +24 | SUS |
| L1-VDC-C1 | U04-A | Electronics | L1-SUS-C1 | -18 | SUS |
| L1-VDC-C1 | U04-B | Electronics | L1-SUS-C1 | +18 | SUS |
| L1-VDC-C1 | U08-A | Electronics | L1-SUS-C2 | -18 | SUS |
| L1-VDC-C1 | U08-B | Electronics | L1-SUS-C2 | +18 | SUS |
| L1-VDC-C1 | U11-A | Electronics | L1-SUS-C3 | -18 | SUS |
| L1-VDC-C1 | U11-B | Electronics | L1-SUS-C3 | +18 | SUS |
| L1-VDC-C1 | U15-A | Electronics | L1-SUS-C4 | -18 | SUS |
| L1-VDC-C1 | U15-B | Electronics | L1-SUS-C4 | +18 | SUS |
| L1-VDC-C1 | U18-A | Electronics | L1-SUS-C4 | -18 | SUS |
| L1-VDC-C1 | U18-B | Electronics | L1-SUS-C4 | +18 | SUS |
| L1-VDC-C1 | U22-A | IO Chassis | L1-SUS-C5 | +24 | SUS |
| L1-VDC-C1 | U22-B | IO Chassis | L1-SUS-C8 | +24 | SUS |
| L1-VDC-C1 | U25-A | Electronics | L1-SUS-C5 | -18 | SUS |
| L1-VDC-C1 | U25-B | Electronics | L1-SUS-C5 | +18 | SUS |
| L1-VDC-C1 | U29-A | Electronics | L1-SUS-C6 | -18 | SUS |
| L1-VDC-C1 | U29-B | Electronics | L1-SUS-C6 | +18 | SUS |
| L1-VDC-C1 | U32-A | Electronics | L1-SUS-C6 | -18 | SUS |
| L1-VDC-C1 | U32-B | Electronics | L1-SUS-C6 | +18 | SUS |
| L1-VDC-C1 | U36-A | Electronics | L1-SUS-C7 | -18 | SUS |
| L1-VDC-C1 | U36-B | Electronics | L1-SUS-C7 | +18 | SUS |
| L1-VDC-C1 | U39-A | Electronics | L1-SUS-C8 | -18 | SUS |
| L1-VDC-C1 | U39-B | Electronics | L1-SUS-C8 | +18 | SUS |
| L1-VDC-C2 | U01-A | IO Chassis | L1-AOS-C1 | +24 | AOS |
| L1-VDC-C2 | U01-B | IO Chassis | L1-PEM-C1 | +24 | DAQ |
| L1-VDC-C2 | U04-A | Electronics | L1-AOS-C1 | -18 | AOS |
| L1-VDC-C2 | U04-B | Electronics | L1-AOS-C1 | +18 | AOS |
| L1-VDC-C2 | U08-A | Electronics | L1-PEM-C1 | -18 | DAQ |
| L1-VDC-C2 | U08-B | Electronics | L1-PEM-C1 | +18 | DAQ |
| L1-VDC-C2 | U11-A | Electronics | L1-ISC-C1 | -24 | ISC |
| L1-VDC-C2 | U11-B | Electronics | L1-ISC-C1 | +24 | ISC |
| L1-VDC-C2 | U15-A | Electronics | L1-ISC-C1 | -18 | ISC |
| L1-VDC-C2 | U15-B | Electronics | L1-ISC-C1 | +18 | ISC |
| L1-VDC-C2 | U18-A | IO Chassis | L1-ISC-C2 | +24 | ISC |
| L1-VDC-C2 | U18-B | IO Chassis | L1-PSL-C1 | +24 | PSL |
| L1-VDC-C2 | U22-A | Electronics | L1-ISC-C2 | -24 | ISC |
| L1-VDC-C2 | U22-B | Electronics | L1-ISC-C2 | +24 | ISC |
| L1-VDC-C2 | U25-A | Electronics | L1-ISC-C2 | -18 | ISC |
| L1-VDC-C2 | U25-B | Electronics | L1-ISC-C2 | +18 | ISC |
| L1-VDC-C2 | U29-A | Electronics | L1-ISC-C3 | -24 | ISC |
| L1-VDC-C2 | U29-B | Electronics | L1-ISC-C3 | +24 | ISC |
| L1-VDC-C2 | U32-A | Electronics | L1-ISC-C3 | -18 | ISC |
| L1-VDC-C2 | U32-B | Electronics | L1-ISC-C3 | +18 | ISC |
| L1-VDC-C2 | U36-A | Electronics | L1-PSL-R1 | -24 | PSL |
| L1-VDC-C2 | U36-B | Electronics | L1-PSL-R1 | +24 | PSL |
| L1-VDC-C2 | U39-A | Electronics | L1-PSL-R1 | -18 | PSL |
| L1-VDC-C2 | U39-B | Electronics | L1-PSL-R1 | +18 | PSL |
| L1-VDC-C3 | U01-A | IO Chassis | L1-SEI-C1 | +24 | SEI |
| L1-VDC-C3 | U01-B | IO Chassis | L1-SEI-C2 | +24 | SEI |
| L1-VDC-C3 | U04-A | High Current | L1-SEI-C1 | -24 | SEI |
| L1-VDC-C3 | U04-B | High Current | L1-SEI-C1 | +24 | SEI |
| L1-VDC-C3 | U08-A | Electronics | L1-SEI-C1 | -18 | SEI |
| L1-VDC-C3 | U08-B | Electronics | L1-SEI-C1 | +18 | SEI |
| L1-VDC-C3 | U11-A | High Current | L1-SEI-C2 | -24 | SEI |
| L1-VDC-C3 | U11-B | High Current | L1-SEI-C2 | +24 | SEI |
| L1-VDC-C3 | U15-A | Electronics | L1-SEI-C2 | -18 | SEI |
| L1-VDC-C3 | U15-B | Electronics | L1-SEI-C2 | +18 | SEI |
| L1-VDC-C3 | U18-A | IO Chassis | L1-SEI-C3 | +24 | SEI |
| L1-VDC-C3 | U18-B | IO Chassis | L1-SEI-C4 | +24 | SEI |
| L1-VDC-C3 | U22-A | High Current | L1-SEI-C3 | -24 | SEI |
| L1-VDC-C3 | U22-B | High Current | L1-SEI-C3 | +24 | SEI |
| L1-VDC-C3 | U25-A | Electronics | L1-SEI-C3 | -18 | SEI |
| L1-VDC-C3 | U25-B | Electronics | L1-SEI-C3 | +18 | SEI |
| L1-VDC-C3 | U29-A | High Current | L1-SEI-C4 | -24 | SEI |
| L1-VDC-C3 | U29-B | High Current | L1-SEI-C4 | +24 | SEI |
| L1-VDC-C3 | U32-A | Electronics | L1-SEI-C4 | -18 | SEI |
| L1-VDC-C3 | U32-B | Electronics | L1-SEI-C4 | +18 | SEI |
| L1-VDC-C3 | U36-A | Electronics | L1-TCS-R1 | -18 | AOS |
| L1-VDC-C3 | U36-B | Electronics | L1-TCS-R1 | +18 | AOS |
| L1-VDC-C3 | U39-A | Electronics | L1-TCS-R2 | -18 | AOS |
| L1-VDC-C3 | U39-B | Electronics | L1-TCS-R2 | +18 | AOS |
| L1-VDC-C4 | U01-A | IO Chassis | L1-SEI-C5 | +24 | SEI |
| L1-VDC-C4 | U01-B | IO Chassis | L1-SEI-C6 | +24 | SEI |
| L1-VDC-C4 | U04-A | High Current | L1-SEI-C5 | -24 | SEI |
| L1-VDC-C4 | U04-B | High Current | L1-SEI-C5 | +24 | SEI |
| L1-VDC-C4 | U08-A | Electronics | L1-SEI-C5 | -18 | SEI |
| L1-VDC-C4 | U08-B | Electronics | L1-SEI-C5 | +18 | SEI |
| L1-VDC-C4 | U11-A | High Current | L1-SEI-C6 | -24 | SEI |
| L1-VDC-C4 | U11-B | High Current | L1-SEI-C6 | +24 | SEI |
| L1-VDC-C4 | U15-A | Electronics | L1-SEI-C6 | -18 | SEI |
| L1-VDC-C4 | U15-B | Electronics | L1-SEI-C6 | +18 | SEI |
| L1-VDC-C4 | U18-A | Electronics | L1-ISC-R1 | -24 | ISC |
| L1-VDC-C4 | U18-B | Electronics | L1-ISC-R1 | +24 | ISC |
| L1-VDC-C4 | U22-A | Electronics | L1-ISC-R1 | -18 | ISC |
| L1-VDC-C4 | U22-B | Electronics | L1-ISC-R1 | +18 | ISC |
| L1-VDC-C4 | U25-A | Electronics | L1-ISC-R2 | -24 | ISC |
| L1-VDC-C4 | U25-B | Electronics | L1-ISC-R2 | +24 | ISC |
| L1-VDC-C4 | U29-A | Electronics | L1-ISC-R2 | -18 | ISC |
| L1-VDC-C4 | U29-B | Electronics | L1-ISC-R2 | +18 | ISC |
| L1-VDC-C4 | U32-A | Electronics | L1-ISC-R3 | -24 | ISC |
| L1-VDC-C4 | U32-B | Electronics | L1-ISC-R3 | +24 | ISC |
| L1-VDC-C4 | U36-A | Electronics | L1-ISC-R3 | -18 | ISC |
| L1-VDC-C4 | U36-B | Electronics | L1-ISC-R3 | +18 | ISC |
| L1-VDC-C4 | U39-A | Electronics | L1-PSL-C1 | -18 | PSL |
| L1-VDC-C4 | U39-B | Electronics | L1-PSL-C1 | +18 | PSL |
| L1-VDC-C5 | U01-A | Electronics | L1-PSL-R2 | -24 | PSL |
| L1-VDC-C5 | U01-B | Electronics | L1-PSL-R2 | +24 | PSL |
| L1-VDC-C5 | U04-A | Electronics | L1-PSL-R2 | -18 | PSL |
| L1-VDC-C5 | U04-B | Electronics | L1-PSL-R2 | +18 | PSL |
| L1-VDC-C5 | U08-A | Electronics | L1-SUS-R1 | -18 | SUS |
| L1-VDC-C5 | U08-B | Electronics | L1-SUS-R1 | +18 | SUS |
| L1-VDC-C5 | U11-A | Electronics | L1-SUS-R2 | -18 | SUS |
| L1-VDC-C5 | U11-B | Electronics | L1-SUS-R2 | +18 | SUS |
| L1-VDC-C5 | U15-A | Electronics | L1-SUS-R3 | -18 | SUS |
| L1-VDC-C5 | U15-B | Electronics | L1-SUS-R3 | +18 | SUS |
| L1-VDC-C5 | U18-A | Electronics | L1-SUS-R4 | -18 | SUS |
| L1-VDC-C5 | U18-B | Electronics | L1-SUS-R4 | +18 | SUS |
| L1-VDC-C5 | U22-A | Electronics | L1-SUS-R5 | -18 | SUS |
| L1-VDC-C5 | U22-B | Electronics | L1-SUS-R5 | +18 | SUS |
| L1-VDC-C5 | U25-A | Electronics | L1-SUS-R6 | -18 | SUS |
| L1-VDC-C5 | U25-B | Electronics | L1-SUS-R6 | +18 | SUS |
| L1-VDC-C5 | U29-A |  |  |  |  |
| L1-VDC-C5 | U29-B |  |  |  |  |
| L1-VDC-C5 | U32-A |  |  |  |  |
| L1-VDC-C5 | U32-B |  |  |  |  |
| L1-VDC-C5 | U36-A |  |  |  |  |
| L1-VDC-C5 | U36-B |  |  |  |  |
| L1-VDC-C5 | U39-A |  |  |  |  |
| L1-VDC-C5 | U39-B |  |  |  |  |
| L1-VDC-C6 | U01-A |  |  |  |  |
| L1-VDC-C6 | U01-B |  |  |  |  |
| L1-VDC-C6 | U04-A |  |  |  |  |
| L1-VDC-C6 | U04-B |  |  |  |  |
| L1-VDC-C6 | U08-A |  |  |  |  |
| L1-VDC-C6 | U08-B |  |  |  |  |
| L1-VDC-C6 | U11-A |  |  |  |  |
| L1-VDC-C6 | U11-B |  |  |  |  |
| L1-VDC-C6 | U15-A |  |  |  |  |
| L1-VDC-C6 | U15-B |  |  |  |  |
| L1-VDC-C6 | U18-A |  |  |  |  |
| L1-VDC-C6 | U18-B |  |  |  |  |
| L1-VDC-C6 | U22-A |  |  |  |  |
| L1-VDC-C6 | U22-B |  |  |  |  |
| L1-VDC-C6 | U25-A |  |  |  |  |
| L1-VDC-C6 | U25-B |  |  |  |  |
| L1-VDC-C6 | U29-A |  |  |  |  |
| L1-VDC-C6 | U29-B |  |  |  |  |
| L1-VDC-C6 | U32-A |  |  |  |  |
| L1-VDC-C6 | U32-B |  |  |  |  |
| L1-VDC-C6 | U36-A |  |  |  |  |
| L1-VDC-C6 | U36-B |  |  |  |  |
| L1-VDC-C6 | U39-A |  |  |  |  |
| L1-VDC-C6 | U39-B |  |  |  |  |
| L1-VDC-XR1 | U01-A | IO Chassis | L1-TCS-XC1 | +24 | AOS |
| L1-VDC-XR1 | U01-B | IO Chassis | L1-PEM-XR1 | +24 | DAQ |
| L1-VDC-XR1 | U04-A | Electronics | L1-TCS-XC1 | -24 | AOS |
| L1-VDC-XR1 | U04-B | Electronics | L1-TCS-XC1 | +24 | AOS |
| L1-VDC-XR1 | U08-A | Electronics | L1-TCS-XC1 | -18 | AOS |
| L1-VDC-XR1 | U08-B | Electronics | L1-TCS-XC1 | +18 | AOS |
| L1-VDC-XR1 | U11-A | Electronics | L1-TCS-XR1 | -24 | AOS |
| L1-VDC-XR1 | U11-B | Electronics | L1-TCS-XR1 | +24 | AOS |
| L1-VDC-XR1 | U15-A | Electronics | L1-TCS-XR1 | -18 | AOS |
| L1-VDC-XR1 | U15-B | Electronics | L1-TCS-XR1 | +18 | AOS |
| L1-VDC-XR1 | U18-A | Electronics | L1-PEM-XR1 | -24 | DAQ |
| L1-VDC-XR1 | U18-B | Electronics | L1-PEM-XR1 | +24 | DAQ |
| L1-VDC-XR1 | U22-A | Electronics | L1-PEM-XR1 | -18 | DAQ |
| L1-VDC-XR1 | U22-B | Electronics | L1-PEM-XR1 | +18 | DAQ |
| L1-VDC-XR1 | U25-A | Electronics | L1-ISC-XR1 | -24 | ISC |
| L1-VDC-XR1 | U25-B | Electronics | L1-ISC-XR1 | +24 | ISC |
| L1-VDC-XR1 | U29-A | Electronics | L1-ISC-XR1 | -18 | ISC |
| L1-VDC-XR1 | U29-B | Electronics | L1-ISC-XR1 | +18 | ISC |
| L1-VDC-XR1 | U32-A |  |  |  |  |
| L1-VDC-XR1 | U32-B |  |  |  |  |
| L1-VDC-XR1 | U36-A |  |  |  |  |
| L1-VDC-XR1 | U36-B |  |  |  |  |
| L1-VDC-XR1 | U39-A |  |  |  |  |
| L1-VDC-XR1 | U39-B |  |  |  |  |
| L1-VDC-XR2 | U01-A | IO Chassis | L1-SEI-XC1 | +24 | SEI |
| L1-VDC-XR2 | U01-B | IO Chassis | L1-SUS-XC2 | +24 | SUS |
| L1-VDC-XR2 | U04-A | High Current | L1-SEI-XC1 | -24 | SEI |
| L1-VDC-XR2 | U04-B | High Current | L1-SEI-XC1 | +24 | SEI |
| L1-VDC-XR2 | U08-A | Electronics | L1-SEI-XC1 | -18 | SEI |
| L1-VDC-XR2 | U08-B | Electronics | L1-SEI-XC1 | +18 | SEI |
| L1-VDC-XR2 | U11-A | Electronics | L1-SUS-XC1 | -18 | SUS |
| L1-VDC-XR2 | U11-B | Electronics | L1-SUS-XC1 | +18 | SUS |
| L1-VDC-XR2 | U15-A | Electronics | L1-SUS-XC2 | -18 | SUS |
| L1-VDC-XR2 | U15-B | Electronics | L1-SUS-XC2 | +18 | SUS |
| L1-VDC-XR2 | U18-A | Electronics | L1-SUS-XR1 | -18 | SUS |
| L1-VDC-XR2 | U18-B | Electronics | L1-SUS-XR1 | +18 | SUS |
| L1-VDC-XR2 | U22-A |  |  |  |  |
| L1-VDC-XR2 | U22-B |  |  |  |  |
| L1-VDC-XR2 | U25-A |  |  |  |  |
| L1-VDC-XR2 | U25-B |  |  |  |  |
| L1-VDC-XR2 | U29-A |  |  |  |  |
| L1-VDC-XR2 | U29-B |  |  |  |  |
| L1-VDC-XR2 | U32-A |  |  |  |  |
| L1-VDC-XR2 | U32-B |  |  |  |  |
| L1-VDC-XR2 | U36-A |  |  |  |  |
| L1-VDC-XR2 | U36-B |  |  |  |  |
| L1-VDC-XR2 | U39-A |  |  |  |  |
| L1-VDC-XR2 | U39-B |  |  |  |  |
| L1-VDC-YR1 | U01-A | IO Chassis | L1-TCS-YC1 | +24 | AOS |
| L1-VDC-YR1 | U01-B | IO Chassis | L1-PEM-YR1 | +24 | DAQ |
| L1-VDC-YR1 | U04-A | Electronics | L1-TCS-YC1 | -24 | AOS |
| L1-VDC-YR1 | U04-B | Electronics | L1-TCS-YC1 | +24 | AOS |
| L1-VDC-YR1 | U08-A | Electronics | L1-TCS-YC1 | -18 | AOS |
| L1-VDC-YR1 | U08-B | Electronics | L1-TCS-YC1 | +18 | AOS |
| L1-VDC-YR1 | U11-A | Electronics | L1-TCS-YR1 | -24 | AOS |
| L1-VDC-YR1 | U11-B | Electronics | L1-TCS-YR1 | +24 | AOS |
| L1-VDC-YR1 | U15-A | Electronics | L1-TCS-YR1 | -18 | AOS |
| L1-VDC-YR1 | U15-B | Electronics | L1-TCS-YR1 | +18 | AOS |
| L1-VDC-YR1 | U18-A | Electronics | L1-PEM-YR1 | -24 | DAQ |
| L1-VDC-YR1 | U18-B | Electronics | L1-PEM-YR1 | +24 | DAQ |
| L1-VDC-YR1 | U22-A | Electronics | L1-PEM-YR1 | -18 | DAQ |
| L1-VDC-YR1 | U22-B | Electronics | L1-PEM-YR1 | +18 | DAQ |
| L1-VDC-YR1 | U25-A | Electronics | L1-ISC-YR1 | -24 | ISC |
| L1-VDC-YR1 | U25-B | Electronics | L1-ISC-YR1 | +24 | ISC |
| L1-VDC-YR1 | U29-A | Electronics | L1-ISC-YR1 | -18 | ISC |
| L1-VDC-YR1 | U29-B | Electronics | L1-ISC-YR1 | +18 | ISC |
| L1-VDC-YR1 | U32-A |  |  |  |  |
| L1-VDC-YR1 | U32-B |  |  |  |  |
| L1-VDC-YR1 | U36-A |  |  |  |  |
| L1-VDC-YR1 | U36-B |  |  |  |  |
| L1-VDC-YR1 | U39-A |  |  |  |  |
| L1-VDC-YR1 | U39-B |  |  |  |  |
| L1-VDC-YR2 | U01-A | IO Chassis | L1-SEI-YC1 | +24 | SEI |
| L1-VDC-YR2 | U01-B | IO Chassis | L1-SUS-YC2 | +24 | SUS |
| L1-VDC-YR2 | U04-A | High Current | L1-SEI-YC1 | -24 | SEI |
| L1-VDC-YR2 | U04-B | High Current | L1-SEI-YC1 | +24 | SEI |
| L1-VDC-YR2 | U08-A | Electronics | L1-SEI-YC1 | -18 | SEI |
| L1-VDC-YR2 | U08-B | Electronics | L1-SEI-YC1 | +18 | SEI |
| L1-VDC-YR2 | U11-A | Electronics | L1-SUS-YC1 | -18 | SUS |
| L1-VDC-YR2 | U11-B | Electronics | L1-SUS-YC1 | +18 | SUS |
| L1-VDC-YR2 | U15-A | Electronics | L1-SUS-YC2 | -18 | SUS |
| L1-VDC-YR2 | U15-B | Electronics | L1-SUS-YC2 | +18 | SUS |
| L1-VDC-YR2 | U18-A | Electronics | L1-SUS-YR1 | -18 | SUS |
| L1-VDC-YR2 | U18-B | Electronics | L1-SUS-YR1 | +18 | SUS |
| L1-VDC-YR2 | U22-A |  |  |  |  |
| L1-VDC-YR2 | U22-B |  |  |  |  |
| L1-VDC-YR2 | U25-A |  |  |  |  |
| L1-VDC-YR2 | U25-B |  |  |  |  |
| L1-VDC-YR2 | U29-A |  |  |  |  |
| L1-VDC-YR2 | U29-B |  |  |  |  |
| L1-VDC-YR2 | U32-A |  |  |  |  |
| L1-VDC-YR2 | U32-B |  |  |  |  |
| L1-VDC-YR2 | U36-A |  |  |  |  |
| L1-VDC-YR2 | U36-B |  |  |  |  |
| L1-VDC-YR2 | U39-A |  |  |  |  |
| L1-VDC-YR2 | U39-B |  |  |  |  |

## Table 2: Power Strips (and Boxes) Required by Rack

Table 2 provides a list of power strips required for the LLO DC Power distribution system.

| Rack Designator | +/-18V Power Strip Count (D1002189 Option 01) | +/-24V Power Strip Count (D1002189 Option 02) | High Current Box Count (D070124) | +24V IO Chassis Count | +24V Power Strip (Short) Count (D110034 Option 02) | Subsystem | Location / Comment |
| --- | --- | --- | --- | --- | --- | --- | --- |
| L1-AOS-C1 | 1 | 0 | 0 | 1 | 1 | AOS | Common Electronics Room |
| L1-TCS-R1 | 1 | 0 | 0 | 0 | 0 | AOS | Remote Electronics Rack |
| L1-TCS-R2 | 1 | 0 | 0 | 0 | 0 | AOS | Remote Electronics Rack |
| L1-TCS-XC1 | 1 | 1 | 0 | 1 | 1 | AOS | X End Remote Electronics Rack |
| L1-TCS-XR1 | 1 | 1 | 0 | 0 | 0 | AOS | X End Remote Electronics Rack |
| L1-TCS-YC1 | 1 | 1 | 0 | 1 | 1 | AOS | Y End Common Electronics Rack |
| L1-TCS-YR1 | 1 | 1 | 0 | 0 | 0 | AOS | Y End Remote Electronics Rack |
| L1-PEM-C1 | 1 | 0 | 0 | 1 | 1 | DAQ | Common Electronics Room |
| L1-ETR-01 | 0 | 0 | 1 | 0 | 0 | DAQ | DAQ Electronics Test Rack |
| L1-PEM-XC1 | 1 | 1 | 0 | 1 | 1 | DAQ/ISC | X End Common Electronics Rack |
| L1-PEM-YC1 | 1 | 1 | 0 | 1 | 1 | DAQ/ISC | Y End Common Electronics Rack |
| L1-ISC-C1 | 1 | 1 | 0 | 0 | 0 | ISC | Common Electronics Room |
| L1-ISC-C2 | 1 | 1 | 0 | 2 | 1 | ISC | Common Electronics Room |
| L1-ISC-C3 | 1 | 1 | 0 | 0 | 0 | ISC | Common Electronics Room |
| L1-ISC-R1 | 1 | 1 | 0 | 0 | 0 | ISC | Remote Electronics Rack |
| L1-ISC-R2 | 1 | 1 | 0 | 0 | 0 | ISC | Remote Electronics Rack |
| L1-ISC-R3 | 1 | 1 | 0 | 0 | 0 | ISC | Remote Electronics Rack |
| L1-ISC-XR1 | 1 | 1 | 0 | 0 | 0 | ISC | X End Remote Electronics Rack |
| L1-ISC-YR1 | 1 | 1 | 0 | 0 | 0 | ISC | Y End Remote Electronics Rack |
| L1-ETR-04 | 0 | 0 | 1 | 0 | 0 | OPTICS | Optics Electronics Lab Test Rack |
| L1-PSL-C1 | 1 | 0 | 0 | 1 | 1 | PSL | Common Electronics Room |
| L1-PSL-R1 | 1 | 1 | 0 | 0 | 0 | PSL | Remote Electronics Rack |
| L1-PSL-R2 | 1 | 1 | 0 | 0 | 0 | PSL | Remote Electronics Rack |
| L1-SEI-C1 | 1 | 0 | 1 | 1 | 1 | SEI | Common Electronics Room |
| L1-SEI-C2 | 1 | 0 | 1 | 1 | 1 | SEI | Common Electronics Room |
| L1-SEI-C3 | 1 | 0 | 1 | 1 | 1 | SEI | Common Electronics Room |
| L1-SEI-C4 | 1 | 0 | 1 | 1 | 1 | SEI | Common Electronics Room |
| L1-SEI-C5 | 1 | 0 | 1 | 1 | 1 | SEI | Common Electronics Room |
| L1-SEI-C6 | 1 | 0 | 1 | 1 | 1 | SEI | Common Electronics Room |
| L1-SEI-XC1 | 1 | 0 | 1 | 1 | 1 | SEI | X End Common Electronics Rack |
| L1-SEI-YC1 | 1 | 0 | 1 | 1 | 1 | SEI | Y End Common Electronics Rack |
| L1-ETR-05 | 0 | 0 | 1 | 0 | 0 | SEI | HAM ISI Electronics Test Rack |
| L1-ETR-07 | 0 | 0 | 1 | 0 | 0 | SEI | Triple Electronics Test Rack |
| L1-SUS-C1 | 1 | 0 | 0 | 0 | 0 | SUS | Common Electronics Room |
| L1-SUS-C2 | 1 | 0 | 0 | 2 | 1 | SUS | Common Electronics Room |
| L1-SUS-C3 | 1 | 0 | 0 | 3 | 1 | SUS | Common Electronics Room |
| L1-SUS-C4 | 2 | 0 | 0 | 0 | 0 | SUS | Common Electronics Room |
| L1-SUS-C5 | 1 | 0 | 0 | 3 | 1 | SUS | Common Electronics Room |
| L1-SUS-C6 | 2 | 0 | 0 | 0 | 0 | SUS | Common Electronics Room |
| L1-SUS-C7 | 1 | 0 | 0 | 0 | 0 | SUS | Common Electronics Room |
| L1-SUS-C8 | 1 | 0 | 0 | 2 | 1 | SUS | Common Electronics Room |
| L1-SUS-R1 | 1 | 0 | 0 | 0 | 0 | SUS | Remote Electronics Rack |
| L1-SUS-R2 | 1 | 0 | 0 | 0 | 0 | SUS | Remote Electronics Rack |
| L1-SUS-R3 | 1 | 0 | 0 | 0 | 0 | SUS | Remote Electronics Rack |
| L1-SUS-R4 | 1 | 0 | 0 | 0 | 0 | SUS | Remote Electronics Rack |
| L1-SUS-R5 | 1 | 0 | 0 | 0 | 0 | SUS | Remote Electronics Rack |
| L1-SUS-R6 | 1 | 0 | 0 | 0 | 0 | SUS | Remote Electronics Rack |
| L1-SUS-XC1 | 1 | 0 | 0 | 0 | 0 | SUS | X End Common Electronics Rack |
| L1-SUS-XC2 | 1 | 0 | 0 | 2 | 1 | SUS | X End Common Electronics Rack |
| L1-SUS-XR1 | 1 | 0 | 0 | 0 | 0 | SUS | X End Remote Electronics Rack |
| L1-SUS-YC1 | 1 | 0 | 0 | 0 | 0 | SUS | Y End Common Electronics Rack |
| L1-SUS-YC2 | 1 | 0 | 0 | 2 | 1 | SUS | Y End Common Electronics Rack |
| L1-SUS-YR1 | 1 | 0 | 0 | 0 | 0 | SUS | Y End Remote Electronics Rack |
| L1-ETR-02 | 0 | 0 | 1 | 0 | 0 | SUS | BSC Electronics Test Rack |
| L1-ETR-03 | 0 | 0 | 1 | 0 | 0 | SUS | RM Electronics Test Rack |
| L1-ETR-06 | 0 | 0 | 1 | 0 | 0 | SUS | STS Huddle Electronics Test Rack |
| L1-VAC-R1 | 0 | 0 | 0 | 0 | 0 | VAC | Remote Electronics Rack |
| L1-VAC-R2 | 0 | 0 | 0 | 0 | 0 | VAC | Remote Electronics Rack |
| L1-VAC-R3 | 0 | 0 | 0 | 0 | 0 | VAC | Remote Electronics Rack |
| L1-VAC-XR1 | 0 | 0 | 0 | 0 | 0 | VAC | X End Remote Electronics Rack |
| L1-VAC-YR1 | 0 | 0 | 0 | 0 | 0 | VAC | Y End Remote Electronics Rack |
| Total Estimate | 51 | 16 | 15 | 31 | 22 |  |  |

## Table 3: DC Cables Required by Rack

The cables needed to connect the power supplies to the power strips for the LLO DC Power distribution system will be built in-situ.  Specifications have been provided in LIGO-G1000552.

# Non-standard Voltages

Non-standard voltages, though not completely discussed in this document, can be implemented using the conventions discussed.  Cable jacket colors have been assigned, as have connector types.  An alternative to running wires for non-standard voltages would be running one of the standard voltages to a step-down transformer within the rack of interest.

# DC Extension Cords

DC extension cords that connect the DC power strips to electronic chassis have been defined and prototyped.  The position that this document takes is that those cables are part of the chassis they serve, and are therefore the responsibility of the chassis provider.