LIGO Laboratory / LIGO Scientific Collaboration

LIGO-T1100047-v3	LIGO	04/16/2011

aLIGO DC Power Supply Requirements

D.Kinzel

Distribution of this document:

LIGO Scientific Collaboration

This is an internal working note

of the LIGO Laboratory.

| California Institute of Technology LIGO Project – MS 18-34 1200 E. California Blvd. Pasadena, CA 91125 Phone (626) 395-2129 Fax (626) 304-9834 E-mail: info@ligo.caltech.edu | Massachusetts Institute of Technology LIGO Project – NW22-295 185 Albany St Cambridge, MA 02139 Phone (617) 253-4824 Fax (617) 253-7014 E-mail: info@ligo.mit.edu |
| --- | --- |
| LIGO Hanford Observatory P.O. Box 1970 Mail Stop S9-02 Richland WA 99352 Phone 509-372-8106 Fax 509-372-8137 | LIGO Livingston Observatory P.O. Box 940 Livingston, LA 70754 Phone 225-686-3100 Fax 225-686-7189 |

http://www.ligo.caltech.edu/

# Introduction

This document describes the requirements of the DC power supplies that are to be used to provide the DC power required to power Advanced LIGO (aLIGO) electronic racks.

# Scope

The scope of this document is to specify the requirements of the DC power supplies required to support aLIGO electronic chasses.  Due to the existence of a variety of power requirements, the scope is limited to a known specific subset of DC power requirements.  Outlying voltage requirements are discussed briefly at the end.

# Requirements for Standard DC Power Supplies for aLIGO Electronics Racks

The following is a list of requirements for the DC Power Supplies intended to source DC power to racks in our electronics rooms.  We intend to provide 4 (four) standard voltages for each electronics rack.  The voltage and current requirements are

- -18VDC @ 20A

- +18VDC @ 20A

- -24VDC @ 20A

- +24VDC @ 20A

For simplicity, the same type of variable power supply can be specified.

- Each supply must be a linear regulated power supply.

- Output requirements:

  - Range: 0-25VDC

  - 20A current

  - Regulation: better than 0.1% no load to full load, 105-125V AC input

  - Ripple: <0.2mV rms, <1mV p-p, 20Hz-10MHz

  - Drift : <0.01% over 8 hours

- Each supply must have a front panel on / off switch.

- Each supply must have a front panel on indicator light.

- Each supply must have front panel readout of both the voltage and the current.

- Each supply must present a 0-10V full-scale voltage monitoring signal and a 0-10V full-scale current monitoring signal.  These monitoring signals should be presented on a rear-mounted DB9 female bulkhead connector according to Figure 1.

- Each supply must have front panel voltage adjustment.

- Each supply must operate in a voltage regulation mode, with front panel current limiting adjustment.

- Mechanical requirements

  - 19 inch rack mountable

  - Standard half-rack form factor (or smaller) for each power supply

  - Maximum 3U height

  - Output connection - rear mounted terminal block or barrier strip

  - Input (120V) connection – either cord or rear mounted terminal block or barrier strip

- Each supply must work over an input voltage range of 105-125VAC @ 47-65Hz

- Each supply must be UL approved.

- Each supply must have fully isolated output with better than 450V of isolation between each terminal and ground.

- Each supply must refrain from exceeding its regulated voltage after an input power failure.

- Each supply must refrain from exceeding its regulated voltage after an input power failure followed by a sudden return of input power.

# Outlying Voltage Requirements

There are a variety of other voltages that are required for aLIGO.  These needs will be addressed on an as-needed basis, with the intent to conform wherever possible to the same requirements listed above.

Figure 1:  Voltage and Current Monitoring Signals