## Slide 1: D1200757 Sequencer – Insertable
Input is from 4 (four) DC Power Supplies: +24VDC, -24VDC, +18VDC, and -18VDC. This sequencer prohibits the 18V supplies from being present prior to the 24V supplies. When the ON/OFF Switch is in the ON position, +24 and -24 are passed to the Output side, and the internal relay switches are closed so that +18 and -18 are passed to the Output side as well.
The relays are operated independently. The +24VDC controls the +18VDC and the -24VDC controls the -18VDC. Output is intended to go to two standard power strips: 0ne +- 24VDC strip and one +-18VDC strip.

## Slide 2: Sequencer – On/Off Switch
SW-3831

## Slide 3: Sequencer – Relay
D06D100

## Slide 4: Sequencer – Connectors
3003W3SXX99A30X

## Slide 5: Sequencer – Connectors
3003W3PXX99A30X
3003W3PXX99A30X are ordered directly from CONEC. It is unusual to have plugs that are panel mounted, but not unheard of. These boxes are intended to be insertable, and thus require these connectors.

## Slide 6: Sequencer – Connectors
303W3CSXX99A30X

## Slide 7: Sequencer – Connectors
303W3CPXX99A30X
303W3CPXX99A30X are ordered directly from CONEC. It is unusual to have plugs that are panel mounted, but not unheard of. These boxes are intended to be insertable, and thus require these connectors.

## Slide 8: Sequencer – Jack Sockets
MDVS44-ND (3341-1S)
x 4 (Kit)

## Slide 9: Sequencer – LED
5100-H5
x 8

## Slide 10: Sequencer – Current Regulator Diode
1N5314
x 8

## Slide 11: Sequencer – Zener Diode
2EZ18D5MSCT-ND
x 2
DIODE ZENER 18V 2W DO-41

## Slide 12: Sequencer – Screws and Nuts for Relays
91099A266
x 4
91831A009
x 4

## Slide 13: Sequencer – Spade Terminals for LEDs
69145K69
x 4
Crimp-on Spade Terminal Block, Vinyl Insulated, 22-18 AWG, #10 Stud

## Slide 14: Sequencer – Spade Terminals for Wires
69145K78
x 8
Crimp-on Spade Terminal Block, Vinyl Insulated, 12-10 AWG, #10 Stud

## Slide 15: Sequencer – Wire Nuts
7108K6
x 2

## Slide 16: Sequencer – Butt Splice
7227K12
x 1

## Slide 17: Sequencer – Layout – Side View
Bottom Plate 8.75” (5U)
Box 7” (4U) x 7” (4U) x 3”
Switch
(Front)
Out
Relay
Plugs
Sockets
In
(Rear)

## Slide 18: Sequencer – Layout – ‘In’ View (Front)
Bottom Plate 8.75” (5U)
Box 7” (4U) x 7” (4U) x 3”
Center at 5.5” x 1.5”
Center at 1.5” x 1.5”
Center at 3.5” x 1.5”
(0,0)
+24
-24
Input
+18
-18
LIGO-D1200757
DC Power Sequencer
On
Off
Switch
Center at 1.25 x 2.25”
0.5”
Center at 5.25 x 2.25”
0.5”

## Slide 19: Sequencer – Layout – ‘Out’ View (Rear)
Bottom Plate 8.75” (5U)
Box 7” (4U) x 7” (4U) x 3”
Center at 5.5” x 1.5”
Center at 1.5” x 1.5”
(0,0)
-18
+18
Output
-24
+24
LIGO-D1200757
DC Power Sequencer
0.5”
Center at 5.25 x 2.25”
0.5”
Center at 1.25 x 2.25”

## Slide 20: Sequencer – Layout – Box Bottom
Box 7” (4U) x 7” (4U) x 3”
Inches
Rack Units
Inches
Hole pattern for Box Bottom:
8 – 6-32 PEM Nuts arranged so that the Bottom Plate can mate with the Box at both 0 degrees and 90 degrees rotation
(0,0)
Out
In

## Slide 21: Sequencer – Layout – Box Top
In
Out
Inches
Inches
(0,0)
Box 7” (4U) x 7” (4U) x 3”
Center at 5.0” x 5.0””
Center at 5.0” x 2.0””
Hole pattern for Box Bottom:
4 – holes as per diagram, – countersunk for 8/32 Phillips flathead screws
1.87” Center to Center
Relay 1
Relay 2

## Slide 22: Sequencer – Layout – Bottom Plate
Bottom Plate 8.75” (5U)
Box 7” (4U) x 7” (4U) x 3”
Inches
Rack Units
Inches
Hole pattern for Bottom Plate:
8 - ¼” holes centered ¼” from edge and centered at the center of every 1U (Rack Unit)
8 – holes arranged so that the Bottom Plate can mate with the Box at both 0 degrees and 90 degrees rotation – countersunk for 6/32 Phillips flathead screws
Out
In

## Slide 23: Hole Pattern for Rack Units
Rack Units
Inches
0.250 (¼”) holes centered at:
0.000 + 0.250 = 0.250
0.000 + 0.875 = 0.875
0.000 + 1.500 = 1.500
1.750 + 0.250 = 2.000
1.750 + 0.875 = 2.375
1.750 + 1.500 = 3.250
3.500 + 0.250 = 3.750
3.500 + 0.875 = 4.365
3.500 + 1.500 = 5.000
5.250 + 0.250 = 5.500
5.250 + 0.875 = 6.125
5.250 + 1.500 = 6.750
7.000 + 0.250 = 7.250
7.000 + 0.875 = 7.875
7.000 + 1.500 = 8.500
8.750 + 0.250 = 9.000
8.750 + 0.875 = 9.375
8.750 + 1.500 = 10.250
0.250
0.875
1.500
1.750
0.625
0.625
0.500
0.000

## Slide 24: Sequencer – Layout – Bottom View
Switch
7
8
9
4
5
6
1
2
3
+18
-18
+18
-18
+24
-24
+24
-24
A1
A2
A3
A1
A2
A3
A1
A2
A3
A1
A2
A3
In
Out
Plugs
Sockets
Relay 1
1
+2
4
+3
Relay 2
1
+2
4
+3
Inches
Inches
Inches

## Slide 25: Sequencer – Layout – Bottom View - bmp

## Slide 26: Sequencer – Layout – 3D

## Slide 27: Sequencer – Layout – Labels
Silk screen labels. Please note carefully the LED labels.
+24
-24
Input
+18
-18
LIGO-D1200757
DC Power Sequencer
-18
+18
Output
-24
+24
On
Off
LIGO-D1200757
DC Power Sequencer

## Slide 28: Sequencer – Schematic

## Slide 29: Sequencer – Wiring
2EZ18D5
1N5314

## Slide 30: D1200757 Sequencer – Internal

## Slide 31: D1200757 Sequencer – Front

## Slide 32: D1200757 Sequencer – Rear