## Slide 1: Prudential Body Box Results
Kate Gushwa
Margot Phelps
Calum Torrie

## Slide 2: Body Box
Series of exercises performed inside an ISO Class 3 box.
Particles collected at knee and sub floor levels.

## Slide 3: Exercises
During each test:
Stand still (1 min)
Reach arms out then touch shoulders (5 min)
Stand still (1 min)
March and touch shoulders (5 min)
Stand still (1 min)
Bend knees (1 min)
Stand still (1 min)

## Slide 4: Constants
Wore:
  Bouffant cap
  Booties
Same activities performed during each test.
Garb removed immediately after tests.
Subjects were tested in the same order to allow a cool down period between tests.

## Slide 5: Constants
Short wait after each test while the particle count stabilized in the empty Body Box.
Subjects had breakfast and drove to Prudential in scrubs to better simulate normal use.

## Slide 6: Prudential Trips
Trip #1
Participants: Calum, Margot, Kate
Tests:
2010 garb w/ scrubs
  LHO hood & new veils
2008 garb w/ scrubs
  LHO hood disposable mask
2010 garb w/ street clothes
  Calum: shorts
  Margot: slacks
  Kate: jeans
*Assume 15-17 washes per year
Trip #2
Participants: Calum, Margot, Kate, Betsy
Tests:
Brand new garb w/ scrubs
  LHO hood (one size fits all)
  New veils (Betsy in mask)
Brand new garb w/ street clothes
  Calum: shorts
  Margot: slacks
  Kate & Betsy: jeans
*Virgin garb washed 3x (customary before first use)

## Slide 7: 2008 Garb
Size of gaps between mask and hood varied between subjects.
Was “best case” test of old garb because subjects had well-fitting hoods.
Sometimes have to wear wrong size at observatories, resulting in bigger gaps.

## Slide 8: 2010 Garb
Calum – hole in suit covered with tape.
Kate – noticeable shedding and loose threads.

## Slide 9: New Garb
Never worn before test.
Washed 3 times.
One size fits all hood (adjustable).

## Slide 10: Scrubs
ESD Micro Denier polyester

## Slide 11: Important Notes
“Adjusted” particle count:
  Initial count (measured before subject entered) subtracted from counts for each activity.
Negative counts:
  In Margot’s 1st test & Kate’s 3rd test, the adjusted particle count for some of the activities was a negative number. The count was zeroed for these cases.
Anomaly:
  Calum was an anomaly. He shed more in 2010 garb (which had a hole) than 2008 garb.

## Slide 12: Interpreting Data
Each subject’s counts (like graph below) were averaged for comparison.
Chart: Margot's Number of 0.3um Particles
| Still (1 min) | Arm Reach (1 min) | Arm Reach (1 min) | Arm Reach (1 min) | Arm Reach (1 min) | Still (1 min) | Marching (1 min) | Marching (1 min) | Marching (1 min) | Marching (1 min) | Still (1 min) | Knee Bends (1 min) | Still (1 min)
2010 garb w/ scrubs | 105.9441 | 70.6294 | 317.8323 | 176.5735 | 317.8323 | 0 | 317.8323 | 494.4058 | 0 | 0 | 0 | 70.6294 | 1094.7557
2008 garb w/ scrubs | 317.8323 | 141.2588 | 1906.9938 | 600.3499 | 353.147 | 176.5735 | 1553.8468 | 247.2029 | 317.8323 | 600.3499 | 247.2029 | 2118.882 | 565.0352
2010 garb w/ street clothes | 3248.9524 | 3213.6377 | 353.147 | 670.9793 | 282.5176 | 1236.0145 | 988.8116 | 1341.9586 | 1059.441 | 247.2029 | 600.3499 | 1871.6791 | 1730.4203
New garb w/ scrubs | 211.8882 | 1094.7557 | 388.4617 | 353.147 | 776.9234 | 1024.1263 | 1341.9586 | 847.5528 | 847.5528 | 988.8116 | 459.0911 | 423.7764 | 1094.7557
New garb w/ street clothes | 105.9441 | 70.6294 | 176.5735 | 0 | 388.4617 | 953.4969 | 600.3499 | 741.6087 | 1165.3851 | 1412.588 | 812.2381 | 670.9793 | 211.8882

## Slide 13: Body Box Averages
Chart: Average Number of 0.3um Particles
| 2010 garb w/ scrubs | 2008 garb w/ scrubs | 2010 garb w/ street clothes | New garb w/ scrubs | New garb w/ street clothes
Calum | 1936.8755 | 1151.8025 | 2393.2501 | 2083.5673 | 2213.96
Grand Mean
Margot | 228.1873 | 703.5775 | 1295.7778 | 757.9078 | 562.3187
Kate | 543.3031 | 1983.0562 | 1464.2018 | 844.8363 | 872.0014
Betsy | 1820.0653 | 1369.1238

## Slide 14: What we’re looking for
 |  | What is it? | What is learned? | How it's evaluated?
Garb | C3 Shedding | Particle generation by C3 garb | How LIGO's garb is holding up. Whether we need to purchase new garb. | New vs. 2010 vs. 2008 garb, constant = scrubs
 | Shielding | Particle penetration through garb | How effectively LIGO's garb contains particles generated by clothes (linting) and people. | New garb vs. 2010 garb, constant = street clothes
Clothing | Scrubs? | Particle generation by clothes worn under garb | Whether implementing scrubs under garb will significantly reduce contamination. | Scrubs vs. street clothes, i) constant = new garb ii) constant = 2010 garb
Note: Can never fully separate variables (ex: shedding, shielding). This is just our best attempt.

## Slide 15: C3 Shedding
New vs. 2010 vs. 2008 garb
constant = scrubs

## Slide 16: C3 Shedding
Chart: Average Number of 0.3um Particles
| New garb w/ scrubs | 2010 garb w/ scrubs | 2008 garb w/ scrubs
Calum | 2083.5673 | 1936.8755 | 1151.8025
Grand Mean
Margot | 757.9078 | 228.1873 | 703.5775
Kate | 844.8363 | 543.3031 | 1983.0562
Grand Mean | 1228.7705 | 902.7886 | 1279.4787
Number of particles per cubic meter
Chart: Average Number of 0.5um Particles
| New garb w/ scrubs | 2010 garb w/ scrubs | 2008 garb w/ scrubs
Calum | 882.8675 | 844.8363 | 437.359
Grand Mean
Margot | 73.3459 | 48.8973 | 81.4955
Kate | 19.0156 | 149.4083 | 448.225
Grand Mean | 325.0763 | 347.714 | 322.3598
Number of particles per cubic meter

## Slide 17: C3 Shedding
Chart: Particle size (um)
| 0.1 | 0.2 | 0.3 | 0.5 | 1 | 5 | 10
ISO 3 (~Class 1) | 1000 | 236.5144 | 101.7625 | 35.1676 | 8.3176 | 0.29251 | 0.069183
ISO 4 (~Class 10) | 10000 | 2365.1441 | 1017.6251 | 351.6757 | 83.1764 | 2.9251 | 0.69183
ISO 5 (~Class 100) | 100000 | 23651.4412 | 10176.2505 | 3516.7572 | 831.7638 | 29.2511 | 6.9183
Calum - new garb w/ scrubs | 2083.5673 | 882.8675 | 393.8947 | 46.1808
Calum - 2010 garb w/ scrubs | 1936.8755 | 844.8363 | 323.2653 | 16.2991
Calum - 2008 garb w/ scrubs | 1151.8025 | 437.359 | 162.9909 | 8.1495
Margot - new garb w/ scrubs | 757.9078 | 73.3459 | 40.7477
Margot - 2010 garb w/ scrubs | 228.1873 | 48.8973
Margot - 2008 garb w/ scrubs | 703.5775 | 81.4955 | 16.2991
Kate - new garb w/ scrubs | 844.8363 | 19.0156 | 2.7165
Kate - 2010 garb w/ scrubs | 543.3031 | 149.4083 | 32.5982
Kate - 2008 garb w/ scrubs | 1983.0562 | 448.225 | 86.9285
Compare blue to blue, red to red, green to green.
In terms of shedding, our old garb is holding up well.

## Slide 18: C3 Shedding
MARGOT: | Avg # of Particles |  |  |  | 
 | 0.3 | 0.5 | 1 | Total Particles | Highest Class
2008 garb w/ scrubs | 704 | 81 | 16 | 10,418 | 4.3
2010 garb w/ scrubs | 228 | 49 | 0 | 3,602 | 4.0
New garb w/ scrubs | 758 | 73 | 41 | 11,336 | 4.4
CALUM: | Avg # of Particles (um) |  |  |  | 
 | 0.3 | 0.5 | 0.1 | Total Particles | Highest Class
2008 garb w/ scrubs | 1,152 | 437 | 163 | 22,884 | 4.8
2010 garb w/ scrubs | 1,937 | 845 | 323 | 40,577 | 5.1
New garb w/ scrubs | 2,084 | 883 | 394 | 44,285 | 5.8
KATE: | Avg # of Particles |  |  |  | 
 | 0.3 | 0.5 | 1 | Total Particles | Highest Class
2008 garb w/ scrubs | 1,983 | 448 | 87 | 32,737 | 4.6
2010 garb w/ scrubs | 543 | 149 | 33 | 9,429 | 4.2
New garb w/ scrubs | 845 | 19 | 3 | 11,265 | 4.5

## Slide 19: Shielding
New garb vs. 2010 garb
constant = street clothes

## Slide 20: Shielding
Number of particles per cubic meter
Number of particles per cubic meter
Chart: Average Number of 0.3um Particles
| New garb w/ street clothes | 2010 garb w/ street clothes
Calum | 2213.96 | 2393.2501
Grand Mean
Margot | 562.3187 | 1295.7778
Kate | 872.0014 | 1464.2018
Grand Mean | 1216.0934 | 1717.7432
Chart: Average Number of 0.5um Particles
| New garb w/ street clothes | 2010 garb w/ street clothes
Calum | 980.6621 | 567.7517
Grand Mean
Margot | 86.9285 | 133.1093
Kate | 165.7074 | 505.2719
Grand Mean | 411.0993 | 402.0443

## Slide 21: Shielding
Chart: Particle size (um)
| 0.1 | 0.2 | 0.3 | 0.5 | 1 | 5 | 10
ISO 3 (~Class 1) | 1000 | 236.5144 | 101.7625 | 35.1676 | 8.3176 | 0.29251 | 0.069183
ISO 4 (~Class 10) | 10000 | 2365.1441 | 1017.6251 | 351.6757 | 83.1764 | 2.9251 | 0.69183
ISO 5 (~Class 100) | 100000 | 23651.4412 | 10176.2505 | 3516.7572 | 831.7638 | 29.2511 | 6.9183
Calum - new garb w/ street clothes | 2213.96 | 980.6621 | 402.0443 | 40.7477 | 8.1495 | 2.7165
Calum - 2010 garb w/ street clothes | 2393.2501 | 567.7517 | 249.9194 | 29.8817 | 2.7165
Margot - new garb w/ street clothes | 562.3187 | 86.9285 | 21.7321
Margot - 2010 garb w/ street clothes | 1295.7778 | 133.1093 | 32.5982 | 2.7165
Kate - new garb w/ street clothes | 872.0014 | 165.7074 | 57.0468 | 2.7165
Kate - 2010 garb w/ street clothes | 1464.2018 | 505.2719 | 89.645
Brand new garb is a better barrier.
Did not test 2008 garb w/ street clothes, so had to use Calum’s anomalous 2010 garb data.

## Slide 22: Scrubs?
Scrubs vs. street clothes
constant = new garb
constant = 2010 garb

## Slide 23: Scrubs vs. Street Clothes (New Garb)
Chart: Average Number of 0.3um Particles
| New garb w/ scrubs | New garb w/ street clothes
Calum | 2083.5673 | 2213.96
Grand Mean
Margot | 757.9078 | 562.3187
Kate | 844.8363 | 872.0014
Betsy | 1820.0653 | 1369.1238
Grand Mean | 1376.5942 | 1254.351
Number of particles per cubic meter
Number of particles per cubic meter
Chart: Average Number of 0.5um Particles
| New garb w/ scrubs | New garb w/ street clothes
Calum | 882.8675 | 980.6621
Grand Mean
Margot | 73.3459 | 86.9285
Kate | 19.0156 | 165.7074
Betsy | 296.1002 | 312.3993
Grand Mean | 317.8323 | 386.4243

## Slide 24: Scrubs vs. Street Clothes (New Garb)
Chart: Particle size (um)
| 0.1 | 0.2 | 0.3 | 0.5 | 1 | 5 | 10
ISO 3 (~Class 1) | 1000 | 236.5144 | 101.7625 | 35.1676 | 8.3176 | 0.29251 | 0.069183
ISO 4 (~Class 10) | 10000 | 2365.1441 | 1017.6251 | 351.6757 | 83.1764 | 2.9251 | 0.69183
ISO 5 (~Class 100) | 100000 | 23651.4412 | 10176.2505 | 3516.7572 | 831.7638 | 29.2511 | 6.9183
Calum - scrubs | 2083.5673 | 882.8675 | 393.8947 | 46.1808
Calum - street clothes | 2213.96 | 980.6621 | 402.0443 | 40.7477 | 8.1495 | 2.7165
Margot - scrubs | 757.9078 | 73.3459 | 40.7477
Margot - street clothes | 562.3187 | 86.9285 | 21.7321
Kate - scrubs | 844.8363 | 19.0156 | 2.7165
Kate - street clothes | 872.0014 | 165.7074 | 57.0468 | 2.7165
Betsy - scrubs | 1820.0653 | 296.1002 | 97.7946
Betsy - street clothes | 1369.1238 | 312.3993 | 92.3615
Kate shed less in scrubs.
Subtler difference for Calum, Margot, and Betsy.
New garb is better at shielding, and masks the contamination from people and clothes. OR new garb sheds more, and masks the benefits of scrubs.

## Slide 25: Scrubs vs. Street Clothes (2010 Garb)
Number of particles per cubic meter
Number of particles per cubic meter
Chart: Average Number of 0.3um Particles
| 2010 garb w/ scrubs | 2010 garb w/ street clothes
Calum* | 1151.8025 | 2393.2501
Grand Mean
Margot | 228.1873 | 1295.7778
Kate | 543.3031 | 1464.2018
Grand Mean | 641.0976 | 1717.7432
Chart: Average Number of 0.5um Particles
| 2010 garb w/ scrubs | 2010 garb w/ street clothes
Calum* | 437.359 | 567.7517
Grand Mean
Margot | 48.8973 | 133.1093
Kate | 149.4083 | 505.2719
Grand Mean | 211.8882 | 402.0443
* Used Calum’s 2008 garb w/ scrubs data due to anomalous test with 2010 garb (had a hole).

## Slide 26: Scrubs vs. Street Clothes (2010 Garb)
Wearing scrubs made a difference in cleanroom class for Margot and Kate.
* Used Calum’s 2008 garb w/ scrubs data due to anomalous test with 2010 garb (had a hole).
Chart: Particle size (um)
| 0.1 | 0.2 | 0.3 | 0.5 | 1 | 5 | 10
ISO 3 (~Class 1) | 1000 | 236.5144 | 101.7625 | 35.1676 | 8.3176 | 0.29251 | 0.069183
ISO 4 (~Class 10) | 10000 | 2365.1441 | 1017.6251 | 351.6757 | 83.1764 | 2.9251 | 0.69183
ISO 5 (~Class 100) | 100000 | 23651.4412 | 10176.2505 | 3516.7572 | 831.7638 | 29.2511 | 6.9183
Calum* - scrubs | 1151.8025 | 437.359 | 162.9909 | 8.1495
Calum - street clothes | 2393.2501 | 567.7517 | 249.9194 | 29.8817 | 2.7165
Margot - scrubs | 228.1873 | 48.8973
Margot - street clothes | 1295.7778 | 133.1093 | 32.5982 | 2.7165
Kate - scrubs | 543.3031 | 149.4083 | 32.5982
Kate - street clothes | 1464.2018 | 505.2719 | 89.645

## Slide 27: Scrubs vs Street Clothes (2010 Garb) Cumulative Results
Graph highlights benefits of scrubs for compounded contamination.
Chart: Cumulative Averages
| 0.3 | 0.5 | 1
Margot - scrubs | 228.1873 | 48.8973 | 0
Grand Mean
Margot - street clothes | 1295.7778 | 133.1093 | 32.5982
Margot & Kate - scrubs | 771.4904 | 198.3056 | 32.5982
Margot & Kate - street clothes | 2759.9796 | 638.3811 | 122.2432
Margot, Kate, Calum* - scrubs | 1923.2929 | 635.6646 | 195.5891
Margot, Kate, Calum - street clothes | 5153.2297 | 1206.1328 | 372.1626

## Slide 28: Further Evidence for Scrubs
Amarak study showed coveralls over street clothes shed more than frocks over scrubs.

## Slide 29: LLO High Bay Particle Count
Chart: Particle Size (um)
| 0.1 | 0.2 | 0.3 | 0.5 | 1 | 5
ISO 3 (~Class 1) | 1000 | 236.5144 | 101.7625 | 35.1676 | 8.3176 | 0.29251
ISO 4 (~Class 10) | 10000 | 2365.1441 | 1017.6251 | 351.6757 | 83.1764 | 2.9251
ISO 5 (~Class 100) | 100000 | 23651.4412 | 10176.2505 | 3516.7572 | 831.7638 | 29.2511
ISO 6 (~Class 1,000) | 1000000 | 236514.4117 | 101762.5053 | 35167.5725 | 8317.6377 | 292.5111
Cleanroom A (SEI): quiescent | 1147.7278 | 353.147
Cleanroom A (SEI): walking 2-3 ft from counter, fully garbed | 4237.764 | 706.294
Cleanroom D (SUS): quiescent | 3531.47 | 1147.7278
Cleanroom D (SUS): shuffling 1 - 2 ft from counter, fully garbed | 6886.3665 | 2648.6025
Cleanroom D (SUS): walking 2-3 ft from counter, fully garbed | 20659.0995 | 6180.0725
People are the largest source of contamination in a cleanroom.

## Slide 30: LLO High Bay vs Margot & Kate
Apples to oranges comparison, but gives idea of scale of improvement.
Chart: Particle Size (um)
| 0.1 | 0.2 | 0.3 | 0.5 | 1 | 5 | 10
ISO 3 (~Class 1) | 1000 | 236.5144 | 101.7625 | 35.1676 | 8.3176 | 0.29251 | 0.069183
ISO 4 (~Class 10) | 10000 | 2365.1441 | 1017.6251 | 351.6757 | 83.1764 | 2.9251 | 0.69183
ISO 5 (~Class 100) | 100000 | 23651.4412 | 10176.2505 | 3516.7572 | 831.7638 | 29.2511 | 6.9183
ISO 6 (~Class 1,000) | 1000000 | 236514.4117 | 101762.5053 | 35167.5725 | 8317.6377 | 292.5111 | 69.1831
Margot- 2010 garb w/ scrubs | 228.1873 | 48.8973
Margot - 2010 garb w/ street clothes | 1295.7778 | 133.1093 | 32.5982 | 2.7165
Kate - 2010 garb w/ scrubs | 543.3031 | 149.4083 | 32.5982
Kate - 2010 garb w/ street clothes | 1464.2018 | 505.2719 | 89.645
Cleanroom A (SEI): quiescent | 1147.7278 | 353.147
Cleanroom A (SEI): walking 2-3 ft from counter, fully garbed | 4237.764 | 706.294
Cleanroom D (SUS): quiescent | 3531.47 | 1147.7278
Cleanroom D (SUS): shuffling 1 - 2 ft from counter, fully garbed | 6886.3665 | 2648.6025

## Slide 31: LLO Banquet Room Particle Count
Chart: Particle Size (um)
| 0.1 | 0.2 | 0.3 | 0.5 | 1 | 5
ISO 3 (~Class 1) | 1000 | 236.5144 | 101.7625 | 35.1676 | 8.3176 | 0.29251
ISO 4 (~Class 10) | 10000 | 2365.1441 | 1017.6251 | 351.6757 | 83.1764 | 2.9251
ISO 5 (~Class 100) | 100000 | 23651.4412 | 10176.2505 | 3516.7572 | 831.7638 | 29.2511
ISO 6 (~Class 1,000) | 1000000 | 236514.4117 | 101762.5053 | 35167.5725 | 8317.6377 | 292.5111
Cleanroom A (Large triple): quiescent | 6427.2754 | 353.147
Cleanroom A: shuffling 1 - 2 ft from counter, fully garbed | 7592.6605 | 353.147
Cleanroom A: walking 2 - 3 ft from counter, fully garbed | 15008.7475 | 353.147
Cleanroom B: quiescent | 882.8675 | 353.147
Cleanroom B: shuffling 1 - 2 ft from counter, full garbed | 1942.3085 | 353.147

## Slide 32: LLO Banquet Room vs Margot & Kate
Chart: Particle Size (um)
| 0.1 | 0.2 | 0.3 | 0.5 | 1 | 5 | 10
ISO 3 (~Class 1) | 1000 | 236.5144 | 101.7625 | 35.1676 | 8.3176 | 0.29251 | 0.069183
ISO 4 (~Class 10) | 10000 | 2365.1441 | 1017.6251 | 351.6757 | 83.1764 | 2.9251 | 0.69183
ISO 5 (~Class 100) | 100000 | 23651.4412 | 10176.2505 | 3516.7572 | 831.7638 | 29.2511 | 6.9183
ISO 6 (~Class 1,000) | 1000000 | 236514.4117 | 101762.5053 | 35167.5725 | 8317.6377 | 292.5111 | 69.1831
Margot- 2010 garb w/ scrubs | 228.1873 | 48.8973
Margot - 2010 garb w/ street clothes | 1295.7778 | 133.1093 | 32.5982 | 2.7165
Kate - 2010 garb w/ scrubs | 543.3031 | 149.4083 | 32.5982
Kate - 2010 garb w/ street clothes | 1464.2018 | 505.2719 | 89.645
Cleanroom A (Large triple): quiescent | 6427.2754 | 353.147
Cleanroom A: shuffling 1 - 2 ft from counter, fully garbed | 7592.6605 | 353.147
Cleanroom A: walking 2 - 3 ft from counter, fully garbed | 15008.7475 | 353.147
Cleanroom B: quiescent | 882.8675 | 353.147

## Slide 33: Conclusions
Garb Shedding:
Old LIGO garb holding up well.
Additional washes may reduce shedding for brand new garb. (Discussing with Prudential)
Garb Shielding:
2010 garb shed 10,300 – 12,500 more particles than new garb (ignoring Calum’s anomalous 2010 data).
New garb is a better barrier.
Scrubs:
Street clothes shed 15,400 – 19,300 more particles than scrubs.
Made a difference in cleanroom class for Margot and Kate.

## Slide 34: Input from Prudential
Garb Shedding:
C3 sheds larger amounts of particles initially.
3 washes brings shedding down to an acceptable level.
Garb sheds less and less up until 20-25 washes, then it sheds again, then it slows again.
Waiting for additional input from test lab.
Garb Shielding:
Fabric weave tightens over time, and there is less penetration between the fibers.
Older garb is a much better barrier than newer garb until the fabric begins to breakdown somewhere above 150 cycles.

## Slide 35: Recommendations
Ideal
Implement scrubs.
  Should offer at least ½ a cleanroom class improvement (log graph, factor of ~3 reduction in particles).
Plan upcoming purchase of new garb.
  Investigating total number of washes before retirement.
Backup
Buy new garb now.
Body Box selection tests or Helmke drum tests (material, type)

## Slide 36
Old Garb in Action at LHO
Best case
Cheek & hair exposed, bouffant cap slipped
Photos highlight effects of movement on garb.

## Slide 37: Old Garb in Action at LHO
Best case
Cheek and hair exposed
Cheek, hair, chin exposed
Photos highlight effects of movement on garb.