LIGO Laboratory / LIGO Scientific Collaboration

LIGO-T1400709-v1	LIGO	November 5, 2014

LLO Beam-Tube Environment Sensor Network

K. Thorne, D. Lormand, M.Fyffe

Distribution of this document:

LIGO Scientific Collaboration

This is an internal working note

of the LIGO Laboratory.

| California Institute of Technology LIGO Project – MS 18-34 1200 E. California Blvd. Pasadena, CA 91125 Phone (626) 395-2129 Fax (626) 304-9834 E-mail: info@ligo.caltech.edu | Massachusetts Institute of Technology LIGO Project – NW22-295 185 Albany St Cambridge, MA 02139 Phone (617) 253-4824 Fax (617) 253-7014 E-mail: info@ligo.mit.edu |
| --- | --- |
| LIGO Hanford Observatory P.O. Box 1970 Mail Stop S9-02 Richland WA 99352 Phone 509-372-8106 Fax 509-372-8137 | LIGO Livingston Observatory P.O. Box 940 Livingston, LA 70754 Phone 225-686-3100 Fax 225-686-7189 |

http://www.ligo.caltech.edu/

# Description

The beam-tube enclosure for each arm of the interferometer has 14 double-doors, 7 on one side of the mid-station, and 7 on the other side of the mid-station.  That makes 28 such locations in all.  At each such location there is a box with two Acromag digitizers.  One is a 961EN (6-channel ADC for analog current readout).  These are used to readout the beam-tube thermocouples and a relative-humidity sensor.  There is also a 962EN (6-channel ADC for analog voltages). These are used for reading out vacuum sensors, etc. as needed.

# References

- Acromag web site http://www.acromag.com

- Acromag 961EN/962EN Data Sheet 961EN_962EN Ethernet Analog Input Modules.pdf

- Acromag 961EN/962EN User’s Manual (Available from website with login)

- Siemens 353 to Modbus TCP/IP Application Note (from Acromag) Siemens_353_to_ModbusTCPIP_App_Note.pdf

# Network Addresses

The Acromag 961ENs are named l0ve<x/y><##>c, where <x/y> is for which arm, the <##> is the double-door label, and ‘c’ to indicate analog current readout

The Acromag 962ENs are named l0ve<x/y><##>v, where <x/y> is for which arm, the <##> is the double-door label, and ‘v’ to indicate analog voltage readout

All these units are on the same VLAN (10.110.60.xxx). This VLAN has a network mask of 255.255.255.0. The VLAN gateway is 10.110.60.1.

| Enclosure Double-Door | 961EN Name | 961EN IP |
| --- | --- | --- |
| X11 | l0vex11c | 10.110.60.171 |
| X12 | l0vex12c | 10.110.60.172 |
| X13 | l0vex13c | 10.110.60.173 |
| X14 | l0vex14c | 10.110.60.174 |
| X15 | l0vex15c | 10.110.60.175 |
| X16 | l0vex16c | 10.110.60.176 |
| X17 | l0vex17c | 10.110.60.177 |
| X21 | l0vex21c | 10.110.60.181 |
| X22 | l0vex22c | 10.110.60.182 |
| X23 | l0vex23c | 10.110.60.183 |
| X24 | l0vex24c | 10.110.60.184 |
| X25 | l0vex25c | 10.110.60.185 |
| X26 | l0vex26c | 10.110.60.186 |
| X27 | l0vex27c | 10.110.60.187 |
| Y11 | l0vey11c | 10.110.60.191 |
| Y12 | l0vey12c | 10.110.60.192 |
| Y13 | l0vey13c | 10.110.60.193 |
| Y14 | l0vey14c | 10.110.60.194 |
| Y15 | l0vey15c | 10.110.60.195 |
| Y16 | l0vey16c | 10.110.60.196 |
| Y17 | l0vey17c | 10.110.60.197 |
| Y21 | l0vey21c | 10.110.60.201 |
| Y22 | l0vey22c | 10.110.60.202 |
| Y23 | l0vey23c | 10.110.60.203 |
| Y24 | l0vey24c | 10.110.60.204 |
| Y25 | l0vey25c | 10.110.60.205 |
| Y26 | l0vey26c | 10.110.60.206 |
| Y27 | l0vey27c | 10.110.60.207 |

# Modbus readout

On the 961ENs, the first channel (CH00) is used for the beam-tube thermocouple readout.  The second channel (CH01) is used for the relative humidity(RH) sensor readout.

The RH sensor uses 4-20mA current-loop readout. Minimum current is 0%, and maximum current is 100%.

For details, see the Acromag manuals.