## Chassis Squeezer 3 Left
Squeezer Controls Chassis 3 |  | Left Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | L | OMRON | DC_1 | 24V | P | TBLOCK
0V | gray | L | OMRON | DC_1 | 0V | P | TBLOCK
24V | violet | L | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | L | EK1101 | 0 | 0V | P | TBLOCK
5V_1 | red | L | EK1101 | 0 | + | P | DC_1 | +V
5VRET_1 | black | L | EK1101 | 0 | – | P | DC_1 | –V
5V_2 | red | L | EL9190 | 4 | + | P | DC_2 | +V
5VRET_2 | black | L | EL9190 | 4 | – | P | DC_2 | –V
24V | violet | L | EL9410 | 11 | 24V | P | TBLOCK
0V | gray | L | EL9410 | 11 | 0V | P | TBLOCK
5V_3 | red | L | EL9410 | 11 | + | P | DC_3 | +V
5VRET_3 | black | L | EL9410 | 11 | – | P | DC_3 | –V
24V | violet | L | OMRON | DC_2 | 24V | P | TBLOCK
0V | gray | L | OMRON | DC_2 | 0V | P | TBLOCK
24V | violet | L | OMRON | DC_3 | 24V | P | TBLOCK
0V | gray | L | OMRON | DC_3 | 0V | P | TBLOCK
Coupler
Input | CAT5 | L | EK1101 | 0 | X2 | Comm. | IN
Output | CAT5 | L | EK1101 | 0 | X2 | Comm. | M/0 | X1
Laser Diagnostics
Laser diode 1 power monitor + | green | L | EL3104 | 1 | +I1 | AI | 11 | 1
Laser diode 1 power monitor – | white | L | EL3104 | 1 | –I1 | AI | 11 | 14
Laser diode 2 power monitor + | green | L | EL3104 | 1 | +I2 | AI | 11 | 2
Laser diode 2 power monitor – | white | L | EL3104 | 1 | –I2 | AI | 11 | 15
Laser crystal, TEC error signal + | green | L | EL3104 | 1 | +I3 | AI | 11 | 3
Laser crystal, TEC error signal – | white | L | EL3104 | 1 | –I3 | AI | 11 | 16
Doubling crystal, TEC error signal + | green | L | EL3104 | 1 | +I4 | AI | 11 | 4
Doubling crystal, TEC error signal – | white | L | EL3104 | 1 | –I4 | AI | 11 | 17
Laser diode 1, TEC error signal + | green | L | EL3104 | 2 | +I1 | AI | 11 | 6
Laser diode 1, TEC error signal – | white | L | EL3104 | 2 | –I1 | AI | 11 | 19
Laser diode 2, TEC error signal + | green | L | EL3104 | 2 | +I2 | AI | 11 | 7
Laser diode 2, TEC error signal – | white | L | EL3104 | 2 | –I2 | AI | 11 | 20
Noise eater monitor + | green | L | EL3104 | 2 | +I3 | AI | 11 | 12
Noise eater monitor – | white | L | EL3104 | 2 | –I3 | AI | 11 | 25
| green | L | EL3104 | 2 | +I4 | AI | 11
| white | L | EL3104 | 2 | –I4 | AI | 11
5V_1 | red | L | EL1124 | 3 | + | P | 11 | VCC
5VRET_1 | black | L | EL1124 | 3 | – | P | 11 | GND
Laser diode 1, temp guard | brown | L | EL1124 | 3 | I1 | BI | 11 | 8
Laser diode 2, temp guard | brown | L | EL1124 | 3 | I2 | BI | 11 | 9
Interlock | brown | L | EL1124 | 3 | I3 | BI | 11 | 13
| brown | L | EL1124 | 3 | I4 | BI | 11
DC PDs SQZ (concentrator 8)
5VRET_2 | black | L | EL2124 | 5 | – | P | 10 | 19
DC PD1 GAIN0 | orange | L | EL2124 | 5 | O1 | BO | 10 | 15
DC PD1 GAIN1 | orange | L | EL2124 | 5 | O2 | BO | 10 | 34
DC PD2 GAIN0 | orange | L | EL2124 | 5 | O3 | BO | 10 | 16
DC PD2 GAIN1 | orange | L | EL2124 | 5 | O4 | BO | 10 | 35
DC PD3 GAIN0 | orange | L | EL2124 | 6 | O1 | BO | 10 | 11
DC PD3 GAIN1 | orange | L | EL2124 | 6 | O2 | BO | 10 | 30
DC PD4 GAIN0 | orange | L | EL2124 | 6 | O3 | BO | 10 | 12
DC PD4 GAIN1 | orange | L | EL2124 | 6 | O4 | BO | 10 | 31
DC PD5 GAIN0 | orange | L | EL2124 | 7 | O1 | BO | 10 | 7
DC PD5 GAIN1 | orange | L | EL2124 | 7 | O2 | BO | 10 | 26
DC PD6 GAIN0 | orange | L | EL2124 | 7 | O3 | BO | 10 | 8
DC PD6 GAIN1 | orange | L | EL2124 | 7 | O4 | BO | 10 | 27
DC PD7 GAIN0 | orange | L | EL2124 | 8 | O1 | BO | 10 | 3
DC PD7 GAIN1 | orange | L | EL2124 | 8 | O2 | BO | 10 | 22
DC PD8 GAIN0 | orange | L | EL2124 | 8 | O3 | BO | 10 | 4
DC PD8 GAIN1 | orange | L | EL2124 | 8 | O4 | BO | 10 | 23
DC PD1 + | green | L | EL3104 | 9 | +I1 | AI | 10 | 13
DC PD1 – | white | L | EL3104 | 9 | –I1 | AI | 10 | 32
DC PD2 + | green | L | EL3104 | 9 | +I2 | AI | 10 | 14
DC PD2 – | white | L | EL3104 | 9 | –I2 | AI | 10 | 33
DC PD3 + | green | L | EL3104 | 9 | +I3 | AI | 10 | 9
DC PD3 – | white | L | EL3104 | 9 | –I3 | AI | 10 | 28
DC PD4 + | green | L | EL3104 | 9 | +I4 | AI | 10 | 10
DC PD4 – | white | L | EL3104 | 9 | –I4 | AI | 10 | 29
DC PD5 + | green | L | EL3104 | 10 | +I1 | AI | 10 | 5
DC PD5 – | white | L | EL3104 | 10 | –I1 | AI | 10 | 24
DC PD6 + | green | L | EL3104 | 10 | +I2 | AI | 10 | 6
DC PD6 – | white | L | EL3104 | 10 | –I2 | AI | 10 | 25
DC PD7 + | green | L | EL3104 | 10 | +I3 | AI | 10 | 1
DC PD7 – | white | L | EL3104 | 10 | –I3 | AI | 10 | 20
DC PD8 + | green | L | EL3104 | 10 | +I4 | AI | 10 | 2
DC PD8 – | white | L | EL3104 | 10 | –I4 | AI | 10 | 21
DC PDs SQZ (concentrator 7)
5VRET_2 | black | L | EL2124 | 12 | – | P | 9 | 19
DC PD1 GAIN0 | orange | L | EL2124 | 12 | O1 | BO | 9 | 11
DC PD1 GAIN1 | orange | L | EL2124 | 12 | O2 | BO | 9 | 30
DC PD2 GAIN0 | orange | L | EL2124 | 12 | O3 | BO | 9 | 12
DC PD2 GAIN1 | orange | L | EL2124 | 12 | O4 | BO | 9 | 31
DC PD3 GAIN0 | orange | L | EL2124 | 13 | O1 | BO | 9 | 7
DC PD3 GAIN1 | orange | L | EL2124 | 13 | O2 | BO | 9 | 26
DC PD4 GAIN0 | orange | L | EL2124 | 13 | O3 | BO | 9 | 8
DC PD4 GAIN1 | orange | L | EL2124 | 13 | O4 | BO | 9 | 27
DC PD5 GAIN0 | orange | L | EL2124 | 14 | O1 | BO | 9 | 3
DC PD5 GAIN1 | orange | L | EL2124 | 14 | O2 | BO | 9 | 22
DC PD6 GAIN0 | orange | L | EL2124 | 14 | O3 | BO | 9 | 4
DC PD6 GAIN1 | orange | L | EL2124 | 14 | O4 | BO | 9 | 23
DC3_RET | black | L | EL3102 | 15 | COM | P | DC3 | –V
DC PD1 + | green | L | EL3102 | 15 | +I1 | AI | 9 | 9
DC PD1 – | white | L | EL3102 | 15 | –I1 | AI | 9 | 28
DC PD2 + | green | L | EL3102 | 15 | +I2 | AI | 9 | 10
DC PD2 – | white | L | EL3102 | 15 | –I2 | AI | 9 | 29
DC PD3 + | green | L | EL3104 | 16 | +I1 | AI | 9 | 5
DC PD3 – | white | L | EL3104 | 16 | –I1 | AI | 9 | 24
DC PD4 + | green | L | EL3104 | 16 | +I2 | AI | 9 | 6
DC PD4 – | white | L | EL3104 | 16 | –I2 | AI | 9 | 25
DC PD5 + | green | L | EL3104 | 16 | +I3 | AI | 9 | 1
DC PD5 – | white | L | EL3104 | 16 | –I3 | AI | 9 | 20
DC PD6 + | green | L | EL3104 | 16 | +I4 | AI | 9 | 2
DC PD6 – | white | L | EL3104 | 16 | –I4 | AI | 9 | 21
PD Monitor 1 + | green | L | EL3104 | 17 | +I1 | AI | 9 | 16
PD Monitor 1 – | white | L | EL3104 | 17 | –I1 | AI | 9 | 35
PD Monitor 2 + | green | L | EL3104 | 17 | +I2 | AI | 9 | 15
PD Monitor 2 – | white | L | EL3104 | 17 | –I2 | AI | 9 | 34
PD Monitor 3 + | green | L | EL3104 | 17 | +I3 | AI | 9 | 14
PD Monitor 3 – | white | L | EL3104 | 17 | –I3 | AI | 9 | 33
PD Monitor 4 + | green | L | EL3104 | 17 | +I4 | AI | 9 | 13
PD Monitor 4 – | white | L | EL3104 | 17 | –I4 | AI | 9 | 32
Temperature Sensors
Temperature Supply 1 + | red | L | EL3692 | 18 | +R1 | AI | 8 | 1-2
Temperature Supply 1 – | black | L | EL3692 | 18 | –R1 | AI | 8 | 1-4
Temperature Readback 1 + | green | L | EL3692 | 18 | +RL1 | AI | 8 | 1-1
Temperature Readback 1 – | white | L | EL3692 | 18 | –RL1 | AI | 8 | 1-3
Temperature Supply 2 + | red | L | EL3692 | 18 | +R2 | AI | 8 | 2-2
Temperature Supply 2 – | black | L | EL3692 | 18 | –R2 | AI | 8 | 2-4
Temperature Readback 2 + | green | L | EL3692 | 18 | +RL2 | AI | 8 | 2-1
Temperature Readback 2 – | white | L | EL3692 | 18 | –RL2 | AI | 8 | 2-3
Temperature Supply 3 + | red | L | EL3692 | 19 | +R1 | AI | 8 | 3-2
Temperature Supply 3 – | black | L | EL3692 | 19 | –R1 | AI | 8 | 3-4
Temperature Readback 3 + | green | L | EL3692 | 19 | +RL1 | AI | 8 | 3-1
Temperature Readback 3 – | white | L | EL3692 | 19 | –RL1 | AI | 8 | 3-3
Temperature Supply 4 + | red | L | EL3692 | 19 | +R2 | AI | 8 | 4-2
Temperature Supply 4 – | black | L | EL3692 | 19 | –R2 | AI | 8 | 4-4
Temperature Readback 4 + | green | L | EL3692 | 19 | +RL2 | AI | 8 | 4-1
Temperature Readback 4 – | white | L | EL3692 | 19 | –RL2 | AI | 8 | 4-3

## Chassis Squeezer 3 Middle
Squeezer Controls Chassis 3 |  | Middle Rail
Name | Color | RaiM | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | M | OMRON | DC_4 | 24V | P | TBLOCK
0V | gray | M | OMRON | DC_4 | 0V | P | TBLOCK
24V | violet | M | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | M | EK1101 | 0 | 0V | P | TBLOCK
5V_4 | red | M | EK1101 | 0 | + | P | DC_4 | +V
5VRET_4 | black | M | EK1101 | 0 | – | P | DC_4 | –V
24V | violet | M | EL9410 | 7 | 24V | P | TBLOCK
0V | gray | M | EL9410 | 7 | 0V | P | TBLOCK
5V_5 | red | M | EL9410 | 7 | + | P | DC_5 | +V
5VRET_5 | black | M | EL9410 | 7 | – | P | DC_5 | –V
24V | violet | M | EL9410 | 16 | 24V | P | TBLOCK
0V | gray | M | EL9410 | 16 | 0V | P | TBLOCK
5V_6 | red | M | EL9410 | 16 | + | P | DC_6 | +V
5VRET_6 | black | M | EL9410 | 16 | – | P | DC_6 | –V
24V | violet | M | OMRON | DC_5 | 24V | P | TBLOCK
0V | gray | M | OMRON | DC_5 | 0V | P | TBLOCK
24V | violet | M | OMRON | DC_6 | 24V | P | TBLOCK
0V | gray | M | OMRON | DC_6 | 0V | P | TBLOCK
Coupler
Output | CAT5 | M | EK1100 | 0 | X2 | Comm. | R/0 | X1
Motorized Flipper/TTL IO
5VRET_4 | black | M | EL1124 | 1 | – | P | 7 | 13
IN 1 | brown | M | EL1124 | 1 | I1 | BI | 7 | 14
IN 2 | brown | M | EL1124 | 1 | I2 | BI | 7 | 15
IN 3 | brown | M | EL1124 | 1 | I3 | BI | 7 | 16
IN 4 | brown | M | EL1124 | 1 | I4 | BI | 7 | 17
IN 5 | brown | M | EL1124 | 2 | I1 | BI | 7 | 18
IN 6 | brown | M | EL1124 | 2 | I2 | BI | 7 | 19
IN 7 | brown | M | EL1124 | 2 | I3 | BI | 7 | 20
IN 8 | brown | M | EL1124 | 2 | I4 | BI | 7 | 21
RELAY 1 MON | brown | M | EL1124 | 3 | I1 | BI | 7 | 22
RELAY 2 MON | brown | M | EL1124 | 3 | I2 | BI | 7 | 23
RELAY 3 MON | brown | M | EL1124 | 3 | I3 | BI | 7 | 24
OK | brown | M | EL1124 | 3 | I4 | BI | 7 | 25
OUT 1 | orange | M | EL2124 | 4 | O1 | BO | 7 | 1
OUT 2 | orange | M | EL2124 | 4 | O2 | BO | 7 | 2
OUT 3 | orange | M | EL2124 | 4 | O3 | BO | 7 | 3
OUT 4 | orange | M | EL2124 | 4 | O4 | BO | 7 | 4
OUT 5 | orange | M | EL2124 | 5 | O1 | BO | 7 | 5
OUT 6 | orange | M | EL2124 | 5 | O2 | BO | 7 | 6
OUT 7 | orange | M | EL2124 | 5 | O3 | BO | 7 | 7
OUT 8 | orange | M | EL2124 | 5 | O4 | BO | 7 | 8
RELAY 1 COIL | orange | M | EL2124 | 6 | O1 | BO | 7 | 9
RELAY 2 COIL | orange | M | EL2124 | 6 | O2 | BO | 7 | 10
RELAY 3 COIL | orange | M | EL2124 | 6 | O3 | BO | 7 | 11
Extra | orange | M | EL2124 | 6 | O4 | BO | 7 | 12
TTFSS
5VRET_5 | black | M | EL1124 | 8 | – | P | 6 | 19
Common excitation state | brown | M | EL1124 | 8 | I1 | BI | 6 | 6
Fast excitation state | brown | M | EL1124 | 8 | I2 | BI | 6 | 25
PFD sign state | brown | M | EL1124 | 8 | I3 | BI | 6 | 7
Supply OK | brown | M | EL1124 | 8 | I4 | BI | 6 | 26
Additive offset enable | orange | M | EL2124 | 9 | O1 | BO | 6 | 1
Boost 1 enable | orange | M | EL2124 | 9 | O2 | BO | 6 | 20
Commen excitation enable | orange | M | EL2124 | 9 | O3 | BO | 6 | 2
Fast excitation enable | orange | M | EL2124 | 9 | O4 | BO | 6 | 21
Ramp enable | orange | M | EL2124 | 10 | O1 | BO | 6 | 3
EOM path enable | orange | M | EL2124 | 10 | O2 | BO | 6 | 22
Phase-freqeuncy descriminator sign | orange | M | EL2124 | 10 | O3 | BO | 6 | 4
Fast path sign | orange | M | EL2124 | 10 | O4 | BO | 6 | 23
Boost 2 enable | orange | M | EL2124 | 11 | O1 | BO | 6 | 5
Boost 3 enable | orange | M | EL2124 | 11 | O2 | BO | 6 | 24
Spare 1 | orange | M | EL2124 | 11 | O3 | BO | 6 | 8
Spare 2 | orange | M | EL2124 | 11 | O4 | BO | 6 | 27
LO power + | green | M | EL3104 | 12 | +I1 | AI | 6 | 9
LO power – | white | M | EL3104 | 12 | –I1 | AI | 6 | 28
RF power + | green | M | EL3104 | 12 | +I2 | AI | 6 | 10
RF power – | white | M | EL3104 | 12 | –I2 | AI | 6 | 29
Mixer + | green | M | EL3104 | 12 | +I3 | AI | 6 | 11
Mixer – | white | M | EL3104 | 12 | –I3 | AI | 6 | 30
EOM RMS value + | green | M | EL3104 | 12 | +I4 | AI | 6 | 12
EOM RMS value – | white | M | EL3104 | 12 | –I4 | AI | 6 | 31
DC6_RET | black | M | EL3102 | 13 | COM | P | DC6 | V-
Fast output + | green | M | EL3102 | 13 | +I1 | AI | 6 | 13
Fast output – | white | M | EL3102 | 13 | –I1 | AI | 6 | 32
| green | M | EL3102 | 13 | +I2 | AI
| white | M | EL3102 | 13 | –I2 | AI
Common gain + | blue | M | EL4134 | 14 | O1 | AO | 6 | 14
Common gain – | yellow | M | EL4134 | 14 | COM | AO | 6 | 33
Common offset + | blue | M | EL4134 | 14 | O2 | AO | 6 | 15
Common offset – | yellow | M | EL4134 | 14 | COM | AO | 6 | 34
Fast gain + | blue | M | EL4134 | 14 | O3 | AO | 6 | 16
Fast gain – | yellow | M | EL4134 | 14 | COM | AO | 6 | 35
Fast offset + | blue | M | EL4134 | 14 | O4 | AO | 6 | 17
Fast offset – | yellow | M | EL4134 | 14 | COM | AO | 6 | 36
Slow + | blue | M | EL4132 | 15 | O1 | AO | 6 | 18
Slow – | yellow | M | EL4132 | 15 | COM | AO | 6 | 37
| blue | M | EL4132 | 15 | O2 | AO
| yellow | M | EL4132 | 15 | COM | AO
AM Modulated AOM Amplifier
Monitor 1 + | green | M | EL3104 | 17 | +I1 | AI | 4 | 1
Monitor 1 – | white | M | EL3104 | 17 | –I1 | AI | 4 | 14
Temp 1 + | green | M | EL3104 | 17 | +I2 | AI | 4 | 4
Temp 1 – | white | M | EL3104 | 17 | –I2 | AI | 4 | 17
Modulation + | green | M | EL3104 | 17 | +I3 | AI | 4 | 10
Modulation – | white | M | EL3104 | 17 | –I3 | AI | 4 | 23
| green | M | EL3104 | 17 | +I4 | AI
| white | M | EL3104 | 17 | –I4 | AI
Bias + | blue | M | EL4132 | 18 | O1 | AO | 4 | 11
Bias – | yellow | M | EL4132 | 18 | COM | AO | 4 | 24
| blue | M | EL4132 | 18 | O2 | AO
| yellow | M | EL4132 | 18 | COM | AO
5VRET_6 | black | M | EL1124 | 19 | – | P | 4 | 20
Excitation switch | brown | M | EL1124 | 19 | I1 | BI | 4 | 9
OK | brown | M | EL1124 | 19 | I2 | BI | 4 | 7
| brown | M | EL1124 | 19 | I3 | BI
| brown | M | EL1124 | 19 | I4 | BI
Excitation enable | orange | M | EL2124 | 20 | O1 | BO | 4 | 8
FSW_A+B | orange | M | EL2124 | 20 | O2 | BO | 4 | 12
FSW_A | orange | M | EL2124 | 20 | O3 | BO | 4 | 25
| orange | M | EL2124 | 20 | O4 | BO

## Chassis Squeezer 3 Right
Squeezer Controls Chassis 3 |  | Right Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin