## Load Summary
How to update these summary tables:
F/G, F and AG columns are directly linked to the "Ansys beam model LRFD cases" tab.
The G columns can be updated by:
1) setting the "include alignment load" parameter to 0 (zero) in cell $K$52 in the "Ansys beam model LRFD cases" tab.
2) copy the AG columns, and then paste special - values only - to the the G columns
3) setting the "include alignment load" parameter back to 1 (one) in cell $K$52 in the "Ansys beam model LRFD cases" tab.
ASCE 7-16 LRFD Load Cases: Forces & Moments on Support Pipe Shoes @FCT CL
Reaction forces are in Newtons (N), Moments are in Newton-meters (Nm).
Maximum Loads (lbf) imposed on Supports at Pipe Centerline
Load Case: | 1.4 D |  | Guided |  | Alt. Guided
| Fixed/Gated | Fixed | min | max | min | max |  | Fixed | Guided
Fx | 0 | 0 | 0 | 0 | 0 | 0 | Maximum Uplift | 0 | 0 | +Fz
Fy | 0 | 0 | -294.4116 | -938.595 | -294.4116 | -938.595 | Maximum Downward | 245.7212 | 602.8703 | -Fz
Fz | 1093.022 | 1093.022 | 841.176 | 2681.7 | 841.176 | 2681.7 | Dead Load | 175.5151 | 430.6216
Mx | 104.8642 | 104.8642 | 0 | 0 | 0 | 0 | Lateral | 122.0488 | 215.3355 | ¦Fx¦
My | 0 | 0 | 0 | 0 | 0 | 0 | Axial | 1699.5066 | 192.7678 | ¦Fy¦
Mz | 0 | 0 | 0 | 0 | 0 | 0
Load Case: | 1.2 D + 1.6 L |  | Guided |  | Alt. Guided
| Fixed/Gated | Fixed | min | max | min | max
Fx | -868.64 | 0 | 0 | 0 | -2206.4 | 3570.24
Fy | 7827.2 | 0 | -252.3528 | -804.51 | -823.8328 | -1576.75
Fz | 936.876 | 936.876 | 721.008 | 2298.6 | 721.008 | 2298.6
Mx | 2595.4196 | 89.8836 | 0 | 0 | 0 | 0
My | 0 | 0 | 0 | 0 | 0 | 0
Mz | 2505.536 | 0 | 0 | 0 | 0 | 0
Load Case: | 1.2 D + Ev + Emhx + L |  | Guided |  | Alt. Guided
| Fixed/Gated | Fixed | min | max | min | max
Fx | -152.49 | 390.41 | 300.46 | 957.86 | -720.04 | 2552.64
Fy | 4892 | 0 | -268.966 | -857.4736 | -626.141 | -1340.1236
Fz | 998.5537 | 998.5537 | 768.4744 | 2449.9245 | 768.4744 | 2449.9245
Mx | 1661.7609 | 95.8009 | 0 | 0 | 0 | 0
My | 0 | 0 | 0 | 0 | 0 | 0
Mz | 1528.5038 | -37.4562 | 0 | 0 | 0 | 0
Load Case: | 1.2 D + Ev + Emhy + L |  | Guided |  | Alt. Guided
| Fixed/Gated | Fixed | min | max | min | max
Fx | -542.9 | 0 | 0 | 0 | -1379 | 2231.4
Fy | 7559.78 | 2667.78 | -268.966 | -857.4736 | -626.141 | -1340.1236
Fz | 998.5537 | 998.5537 | 768.4744 | 2449.9245 | 768.4744 | 2449.9245
Mx | 1661.7609 | 95.8009 | 0 | 0 | 0 | 0
My | 0 | 0 | 0 | 0 | 0 | 0
Mz | 1565.96 | 0 | 0 | 0 | 0 | 0
Load Case: | 0.9 D - Ev + Emhx |  | Guided |  | Alt. Guided
| Fixed/Gated | Fixed | min | max | min | max
Fx | 390.41 | 390.41 | 300.46 | 957.86 | 300.46 | 957.86
Fy | 0 | 0 | -172.6514 | -550.4189 | -172.6514 | -550.4189
Fz | 640.9793 | 640.9793 | 493.2896 | 1572.6255 | 493.2896 | 1572.6255
Mx | 61.4954 | 61.4954 | 0 | 0 | 0 | 0
My | 0 | 0 | 0 | 0 | 0 | 0
Mz | -37.4562 | -37.4562 | 0 | 0 | 0 | 0
Load Case: | 0.9 D - Ev + Emhy |  | Guided |  | Alt. Guided
| Fixed/Gated | Fixed | min | max | min | max
Fx | 0 | 0 | 0 | 0 | 0 | 0
Fy | -2667.78 | -2667.78 | -172.6514 | -550.4189 | -172.6514 | -550.4189
Fz | 640.9793 | 640.9793 | 493.2896 | 1572.6255 | 493.2896 | 1572.6255
Mx | 61.4954 | 61.4954 | 0 | 0 | 0 | 0
My | 0 | 0 | 0 | 0 | 0 | 0
Mz | 0 | 0 | 0 | 0 | 0 | 0

## Ansys beam model LRFD cases
FEA: | FCT beam approx 3
CAD: | NA
Single repeating section with assumed fixed boundary conditions at the Fixed Support (type E)
|  | This beam analysis plus support compliance matrix approach has neglected the mass (weight) of the supports, which tends to reduce any tensile anchor loads. | [43 empty] | Some FEA notes:
FCT Forces & Moments for individual loads (at the FCT centerline): | [45 empty] | Z (m) | dZ (m) | dZ (in)
[46 empty] | 19.6 | 4.6 | 181.1024
Load Case: |  | D (dead load), 1 g vertical + axial due to friction on G supports | [5 empty] | Fixed/Gated | Fixed | Guided | [35 empty] | 15 | 1.5 | 59.0551 | D | displ5
FEA | IFO | E1 | A | B | C | D | E2 | E1 + E2 |  | Min | Max | [34 empty] | 13.5 | 0.4 | 15.748
Fx | Fx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [34 empty] | 13.1 | 3 | 118.1102
Fy | Fz | 550.02 | 642.4 | 600.84 | 1395.4 | 1915.5 | 230.71 | 780.73 | 780.73 | 600.84 | 1915.5 | [34 empty] | 10.1 | 3.09 | 121.6535 | C | displ4
Fz | -Fy | 0 | 224.84 | 210.294 | 488.39 | 670.425 | 0 | 0 | 0 | 210.294 | 670.425 | [34 empty] | 7.01 | 1.52 | 59.8425 | (conflat)
Mx | Mx | 107.95 | 0 | 0 | 0 | 0 | -33.047 | 74.903 | 74.903 | 0 | 0 | [34 empty] | 5.49 | 3.56 | 140.1575 | B | displ3
My | Mz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [34 empty] | 1.93 | 1.016 | 40 | A | displ2
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [34 empty] | 0.914 | 0.508 | 20 | spring | displ
[46 empty] | 0.406 | 0.203 | 7.9921
Load Case: |  | Lvac (atm-vacuum pressure load), 4892 N for Fixed/Gated only | [5 empty] | Fixed/Gated | Fixed | Guided | [35 empty] | 0.203 | 0.203 | 7.9921
FEA | IFO | E1 | A | B | C | D | E2 | E1 + E2 |  | Min | Max | [34 empty] | 0
Fx | Fx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fy | Fz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fz | -Fy | -4892 | 0 | 0 | 0 | 0 | 0 | -4892 | 0 | 0 | 0
Mx | Mx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
My | Mz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Case: |  | Lalign (align the FCT) and associated axial friction | [5 empty] | Fixed/Gated | Fixed | Guided | [14 empty] | static re-alignment of FCT due to non-parallelism of Conflats at tube ends:
FEA | IFO | E1 | A | B | C | D | E2 | E1 + E2 |  | Min | Max | [13 empty] | Guide A: |  | 32.5 mm in X
Fx | Fx | -1394.5 | 2231.4 | -1020.5 | 710.88 | -1379 | 851.6 | -542.9 | -542.9 | -1379 | 2231.4 | [13 empty] | Guide B: |  | 21.9 mm in X
Fy | Fz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | Guide C: |  | 9.6 mm in X
Fz | -Fy | 0 | 780.99 | 357.175 | 248.808 | 482.65 | 0 | 0 | 0 | 248.808 | 780.99 | [13 empty] | Guide D: |  | 0 in X and Y
Mx | Mx | 283.36 | 0 | 0 | 0 | 0 | 1282.6 | 1565.96 | 1565.96 | 0 | 0
My | Mz | 283.36 | 0 | 0 | 0 | 0 | 1282.6 | 1565.96 | 1565.96 | 0 | 0 | [13 empty] | Guide FZ == µ * Sqrt(Fx^2+Fy^2), where µ = friction coeff.
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Case: |  | Ehx (lateral earthquake), .25 g | [5 empty] | Fixed/Gated | Fixed | Guided
FEA | IFO | E1 | A | B | C | D | E2 | E1 + E2 |  | Min | Max
Fx | Fx | 137.52 | 160.62 | 150.23 | 348.89 | 478.93 | 57.685 | 195.205 | 195.205 | 150.23 | 478.93
Fy | Fz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fz | -Fy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mx | Mx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
My | Mz | -26.991 | 0 | 0 | 0 | 0 | 8.2629 | -18.7281 | -18.7281 | 0 | 0
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Case: |  | Ehy (axial earthquake), .25 g | [5 empty] | Fixed/Gated | Fixed | Guided
FEA | IFO | E1 | A | B | C | D | E2 | E1 + E2 |  | Min | Max
Fx | Fx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fy | Fz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fz | -Fy | 137.49 | 0 | 0 | 0 | 0 | 1196.4 | 1333.89 | 1333.89 | 0 | 0
Mx | Mx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
My | Mz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| For Alternate Guided (AG) Supports include the Alignment Load by inserting a 1 (one) here: | [8 empty] | 1
| coefficient of friction on Guided (G) & Alt. Guided (AG) Supports used to develop axial load: | [8 empty] | 0.35
ASCE 7-16 LRFD Load Cases: Forces & Moments on Supports @FCT CL | [18 empty] | LRFD Load Cases: Forces @ 8 Anchors, 17" x 36" baseplate, stiffened X & Y: | [27 empty] | LRFD Load Cases: Forces @ 4 Anchors, 17" x 36" baseplate, stiffened X & Y: | [15 empty] | LRFD Load Cases: Forces @ 4 Anchors, 17" x 24" baseplate, stiffened X & Y: | [15 empty] | LRFD Load Cases: Forces @ 4 Anchors, 17" x 24" baseplate, not stiffened: | [15 empty] | LRFD Load Cases: Forces @ 4 Anchors, 14" x 14" baseplate, stiffened: | [15 empty] | LRFD Load Cases: Forces @ 4 Anchors, 14" x 25" baseplate, stiffened:
| Linear superposition of the anchor loads from each of the above individual load cases, with the indicated load factors | [17 empty] | Transfer of loads at top of support to anchor bolt forces | [27 empty] | Transfer of loads at top of support to anchor bolt forces | [15 empty] | Transfer of loads at top of support to anchor bolt forces | [15 empty] | Transfer of loads at top of support to anchor bolt forces | [15 empty] | Transfer of loads at top of support to anchor bolt forces | [15 empty] | Transfer of loads at top of support to anchor bolt forces
[95 empty] | concept 4 | [15 empty] | concept 6
Load Case: | 1.4 D (1.4 x dead load), incl. axial friction | [6 empty] | Fixed/Gated | Fixed | Guided
FEA | IFO | E1 | A | B | C | D | E2 |  |  | Min | Max | Fx | Fy | Fz | Mx | My | Mz |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 | Fx5 | Fy5 | Fz5 | Fx6 | Fy6 | Fz6 | Fx7 | Fy7 | Fz7 | Fx8 | Fy8 | Fz8 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
Fx | Fx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1093.022 | 0 | 104.8642 | 0 | 0 | FIXED/GATED | 1.0721 | 4.561 | 0.25463 | 1.9001 | -192.7386 | 2.3082 | 3.6094 | -260.7251 | -2.0409 | 6.194 | -97.8597 | -0.53064 | -1.0642 | 4.563 | 0.25965 | -1.8977 | -192.1954 | 2.4148 | -3.6508 | -261.0445 | -2.0816 | -6.1628 | -97.5872 | -0.5841 |  |  |  |  | 9.2937 | -210.6196 | 6.6098 | 14.876 | -336.1209 | -6.5044 | -9.2513 | -210.7443 | 6.5441 | -14.9173 | -335.5262 | -6.6494 |  |  |  |  | 13.0553 | -372.5125 | -5.6791 | 5.6991 | -174.1245 | 5.6815 | -13.0562 | -370.6755 | -5.7423 | -5.6982 | -175.6986 | 5.74 |  |  |  |  | 10.5585 | -372.5098 | -23.8506 | 4.0071 | -175.1072 | 23.6511 | -10.4269 | -371.0402 | -23.4187 | -4.1387 | -174.3538 | 23.6182 |  |  |  |  | 8.4242 | -459.9102 | -4.4744 | 0.65474 | -86.1854 | 4.5339 | -8.4886 | -461.762 | -4.6797 | -0.59035 | -85.1429 | 4.6202 |  |  |  |  | 10.546 | -367.4901 | -4.4949 | 5.0688 | -179.2395 | 4.387 | -10.4924 | -366.7147 | -4.1147 | -5.1224 | -179.5668 | 4.2227
Fy | Fz | 770.028 | 899.36 | 841.176 | 1953.56 | 2681.7 | 322.994 | 1093.022 | 1093.022 | 841.176 | 2681.7 | 0 | 1093.022 | 0 | 104.8642 | 0 | 0 | FIXED | 1.0721 | 4.561 | 0.25463 | 1.9001 | -192.7386 | 2.3082 | 3.6094 | -260.7251 | -2.0409 | 6.194 | -97.8597 | -0.53064 | -1.0642 | 4.563 | 0.25965 | -1.8977 | -192.1954 | 2.4148 | -3.6508 | -261.0445 | -2.0816 | -6.1628 | -97.5872 | -0.5841 |  |  |  |  | 9.2937 | -210.6196 | 6.6098 | 14.876 | -336.1209 | -6.5044 | -9.2513 | -210.7443 | 6.5441 | -14.9173 | -335.5262 | -6.6494 |  |  |  |  | 13.0553 | -372.5125 | -5.6791 | 5.6991 | -174.1245 | 5.6815 | -13.0562 | -370.6755 | -5.7423 | -5.6982 | -175.6986 | 5.74 |  |  |  |  | 10.5585 | -372.5098 | -23.8506 | 4.0071 | -175.1072 | 23.6511 | -10.4269 | -371.0402 | -23.4187 | -4.1387 | -174.3538 | 23.6182 |  |  |  |  | 8.4242 | -459.9102 | -4.4744 | 0.65474 | -86.1854 | 4.5339 | -8.4886 | -461.762 | -4.6797 | -0.59035 | -85.1429 | 4.6202 |  |  |  |  | 10.546 | -367.4901 | -4.4949 | 5.0688 | -179.2395 | 4.387 | -10.4924 | -366.7147 | -4.1147 | -5.1224 | -179.5668 | 4.2227
Fz | -Fy | 0 | 314.776 | 294.4116 | 683.746 | 938.595 | 0 | 0 | 0 | 294.4116 | 938.595 | 0 | 841.176 | 294.4116 | 0 | 0 | 0 | GUIDED (min) | -9.9669 | 222.6997 | -36.7057 | -2.1653 | -6.7475 | -34.439 | 6.2863 | -343.6439 | -37.8526 | 15.6107 | -293.0977 | -37.9723 | 10.0626 | 221.9321 | -36.9377 | 2.2924 | -7.1778 | -34.6071 | -6.4325 | -343.0778 | -37.7293 | -15.6876 | -292.0693 | -38.165 |  |  |  |  | -4.5386 | 103.8221 | -67.61 | 23.3558 | -524.5868 | -79.1282 | 4.7677 | 102.8338 | -68.2086 | -23.584 | -523.2367 | -79.4618 |  |  |  |  | 25.7415 | -705.4775 | -78.1468 | -11.2289 | 284.818 | -68.9084 | -25.8761 | -700.6828 | -78.2664 | 11.3634 | 280.2041 | -69.09 |  |  |  |  | 21.4052 | -705.0863 | -92.5348 | -10.3734 | 283.6193 | -54.978 | -21.4076 | -703.7783 | -91.538 | 10.3757 | 284.0483 | -55.3578 |  |  |  |  | 23.1591 | -1146.75 | -76.2841 | -16.4058 | 726.4817 | -70.9567 | -22.9976 | -1155.2585 | -77.4084 | 16.2446 | 734.3593 | -69.7624 |  |  |  |  | 19.8756 | -681.7563 | -77.2391 | -8.1776 | 261.0001 | -70.4919 | -19.6497 | -680.1034 | -76.1125 | 7.952 | 259.6921 | -70.5682
Mx | Mx | 151.13 | 0 | 0 | 0 | 0 | -46.2658 | 104.8642 | 104.8642 | 0 | 0
My | Mz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2681.7 | 938.595 | 0 | 0 | 0 | GUIDED (max) | -31.7748 | 709.9747 | -117.0191 | -6.903 | -21.5113 | -109.7928 | 20.041 | -1095.5495 | -120.6754 | 49.7674 | -934.4062 | -121.0571 | 32.08 | 707.5277 | -117.7588 | 7.3083 | -22.8829 | -110.3286 | -20.5071 | -1093.7448 | -120.2823 | -50.0128 | -931.1278 | -121.6715 |  |  |  |  | -14.4694 | 330.9888 | -215.5432 | 74.459 | -1672.402 | -252.2638 | 15.1997 | 327.8378 | -217.4515 | -75.1867 | -1668.0979 | -253.3271 |  |  |  |  | 82.065 | -2249.0882 | -249.1348 | -35.7983 | 908.0102 | -219.6825 | -82.4941 | -2233.8025 | -249.5161 | 36.2271 | 893.3011 | -220.2614 |  |  |  |  | 68.2407 | -2247.8412 | -295.0044 | -33.0709 | 904.1888 | -175.2719 | -68.2481 | -2243.6711 | -291.8266 | 33.0782 | 905.5565 | -176.4827 |  |  |  |  | 73.832 | -3655.8812 | -243.1964 | -52.3024 | 2316.0502 | -226.2127 | -73.3171 | -3683.0066 | -246.7808 | 51.7885 | 2341.1643 | -222.4052 |  |  |  |  | 63.3641 | -2173.4642 | -246.2409 | -26.0705 | 832.0779 | -224.7308 | -62.644 | -2168.1947 | -242.6493 | 25.3513 | 827.9078 | -224.974
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Case: | 1.2 D + 1.6 (Lvac + Lalign), incl. transverse align force induced axial friction | [6 empty] | Fixed/Gated | Fixed | Guided
FEA | IFO | E1 | A | B | C | D | E2 |  |  | Min | Max | Fx | Fy | Fz | Mx | My | Mz |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 | Fx5 | Fy5 | Fz5 | Fx6 | Fy6 | Fz6 | Fx7 | Fy7 | Fz7 | Fx8 | Fy8 | Fz8 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
Fx | Fx | -2231.2 | 3570.24 | -1632.8 | 1137.408 | -2206.4 | 1362.56 | -868.64 | 0 | -2206.4 | 3570.24 | -868.64 | 936.876 | -7827.2 | 2595.4196 | 2505.536 | 0 | FIXED/GATED | -618.8182 | -5375.1587 | 1396.558 | -147.2166 | -6048.5182 | 1429.3627 | 364.1478 | 1253.0359 | 1370.2896 | 854.949 | 5342.0306 | 1421.2423 | -1186.5525 | -5895.5314 | 568.5501 | -339.107 | -1567.669 | 503.0188 | 539.2967 | 5663.9548 | 555.0666 | 1401.9245 | 5691.0119 | 583.0592 |  |  |  |  | -739.5983 | -8969.4105 | 2547.9651 | 1195.4479 | 4142.2225 | 2407.6594 | -1371.3778 | -5077.3913 | 1338.5201 | 1784.1605 | 8967.7152 | 1532.9858 |  |  |  |  | 1451.7213 | 8092.085 | 2962.6089 | -1001.6044 | -12922.4959 | 3101.9679 | 2237.8526 | 12774.2721 | 960.3358 | -1819.3132 | -8881.5105 | 802.2875 |  |  |  |  | 1519.6124 | 8247.9974 | 2933.1095 | -1058.5961 | -13079.1329 | 3143.9542 | 2166.1119 | 12681.2127 | 962.3059 | -1758.5055 | -8786.1611 | 787.7271 |  |  |  |  | 2011.0029 | 17259.8383 | 4095.9257 | -1573.4458 | -23279.4308 | 4288.2963 | 2871.3392 | 23005.7193 | -220.1351 | -2440.2728 | -17922.7339 | -336.887 |  |  |  |  | 1717.4505 | 6838.8186 | 2778.7341 | -1255.8554 | -12859.405 | 2927.5941 | 2296.1832 | 13071.8209 | 1124.0297 | -1889.1886 | -7988.0761 | 996.8671
Fy | Fz | 660.024 | 770.88 | 721.008 | 1674.48 | 2298.6 | 276.852 | 936.876 | 936.876 | 721.008 | 2298.6 | 0 | 936.876 | 0 | 89.8836 | 0 | 0 | FIXED | 0.91893 | 3.9094 | 0.21825 | 1.6286 | -165.2045 | 1.9785 | 3.0937 | -223.4786 | -1.7494 | 5.3091 | -83.8797 | -0.45483 | -0.91215 | 3.9112 | 0.22256 | -1.6266 | -164.7389 | 2.0698 | -3.1292 | -223.7524 | -1.7842 | -5.2824 | -83.6462 | -0.50066 |  |  |  |  | 7.966 | -180.5311 | 5.6655 | 12.7509 | -288.1036 | -5.5752 | -7.9297 | -180.638 | 5.6092 | -12.7863 | -287.5939 | -5.6995 |  |  |  |  | 11.1902 | -319.2964 | -4.8678 | 4.8849 | -149.2495 | 4.8698 | -11.191 | -317.7219 | -4.922 | -4.8842 | -150.5988 | 4.92 |  |  |  |  | 9.0501 | -319.2941 | -20.4434 | 3.4347 | -150.0919 | 20.2724 | -8.9373 | -318.0345 | -20.0732 | -3.5475 | -149.4461 | 20.2442 |  |  |  |  | 7.2207 | -394.2088 | -3.8352 | 0.56121 | -73.8732 | 3.8862 | -7.2759 | -395.796 | -4.0111 | -0.50601 | -72.9796 | 3.9601 |  |  |  |  | 9.0394 | -314.9915 | -3.8528 | 4.3447 | -153.6339 | 3.7603 | -8.9935 | -314.3269 | -3.5269 | -4.3906 | -153.9144 | 3.6194
Fz | -Fy | -7827.2 | 1519.392 | 823.8328 | 984.1608 | 1576.75 | 0 | -7827.2 | 0 | 823.8328 | 1576.75 | -2206.4 | 721.008 | 823.8328 | 0 | 0 | 0 | GUIDED (min) | 241.3586 | 803.9568 | -104.3327 | 264.7023 | -5334.9883 | -23.1196 | 287.8122 | -6269.2699 | -177.8467 | 315.2308 | -639.1592 | -106.8397 | 311.864 | 598.1226 | -103.6323 | 285.519 | 5946.1781 | -179.898 | 261.3785 | 5022.8544 | -25.3845 | 238.5336 | -848.8172 | -102.7693 |  |  |  |  | 516.7151 | -4840.3505 | 23.4419 | 599.9699 | -6595.771 | -438.6054 | 585.0512 | 6235.0223 | -424.658 | 504.6425 | 4480.0984 | 16.019 |  |  |  |  | 605.9756 | -7146.3194 | -405.0663 | 503.9324 | -4292.0818 | -8.248 | 498.3115 | 4028.067 | -16.5432 | 598.1583 | 6689.4158 | -393.9753 |  |  |  |  | 605.6569 | -7076.3936 | -483.7923 | 506.1319 | -4365.6824 | 72.5054 | 496.7084 | 3950.729 | 39.4096 | 597.8587 | 6770.2638 | -451.9473 |  |  |  |  | 607.3477 | -9848.4893 | -353.9111 | 503.089 | -4611.5192 | -57.4709 | 495.4903 | 4223.5169 | -61.6051 | 600.4517 | 9515.4909 | -350.8457 |  |  |  |  | 595.3737 | -8562.8631 | -401.7973 | 519.0683 | -5900.432 | -9.186 | 507.3844 | 5568.476 | -22.3595 | 584.5303 | 8173.8183 | -390.49
Mx | Mx | 582.916 | 0 | 0 | 0 | 0 | 2012.5036 | 2595.4196 | 89.8836 | 0 | 0
My | Mz | 453.376 | 0 | 0 | 0 | 0 | 2052.16 | 2505.536 | 0 | 0 | 0 | 3570.24 | 2298.6 | 1576.75 | 0 | 0 | 0 | GUIDED (max) | -505.1705 | 1108.2583 | -195.68 | -461.9334 | 9571.6827 | -312.6815 | -415.8269 | 7752.5904 | -76.7319 | -371.9585 | -1655.5303 | -200.5236 | -389.1082 | 1432.7152 | -199.0079 | -427.1135 | -8690.3955 | -61.1794 | -474.1258 | -10511.4565 | -322.062 | -525.0047 | -1306.3216 | -208.8711 |  |  |  |  | -934.5936 | 10070.8495 | -735.5736 | -793.5726 | 6700.9015 | -43.4152 | -846.141 | -7860.8837 | -15.9596 | -995.8948 | -11209.4444 | -781.8216 |  |  |  |  | -767.6803 | 5805.8172 | -91.8437 | -968.0996 | 10970.2257 | -692.8172 | -1020.5068 | -12233.291 | -721.3733 | -813.9179 | -6841.1712 | -70.7155 |  |  |  |  | -801.5379 | 5697.1644 | -26.3238 | -953.2978 | 11081.1587 | -765.3528 | -982.7482 | -12139.5671 | -864.6851 | -832.5847 | -6937.4907 | 79.6275 |  |  |  |  | -773.8885 | 5813.9527 | -161.244 | -996.324 | 15852.8824 | -628.4623 | -1008.9113 | -17039.7847 | -644.9397 | -791.0789 | -6925.6275 | -142.104 |  |  |  |  | -801.3969 | 8331.1067 | -93.3091 | -955.7496 | 13339.0366 | -701.6749 | -980.8198 | -14521.4571 | -697.5056 | -832.2007 | -9447.2632 | -84.2604
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Case: | 1.279 D + 2 Ehx + (Lvac + Lalign) | [6 empty] | Fixed/Gated | Fixed | Guided
FEA | IFO | E1 | A | B | C | D | E2 |  |  | Min | Max | Fx | Fy | Fz | Mx | My | Mz |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 | Fx5 | Fy5 | Fz5 | Fx6 | Fy6 | Fz6 | Fx7 | Fy7 | Fz7 | Fx8 | Fy8 | Fz8 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
Fx | Fx | -1119.46 | 2552.64 | -720.04 | 1408.66 | -421.14 | 966.97 | -152.49 | 390.41 | -720.04 | 2552.64 | -152.49 | 998.5537 | -4892 | 1661.7609 | 1528.5038 | 0 | FIXED/GATED | -419.9194 | -3380.7478 | 866.9081 | -134.6888 | -2852.4257 | 874.1955 | 175.2789 | 1683.4216 | 862.432 | 472.4212 | 3285.5759 | 881.9558 | -776.0708 | -3663.1233 | 361.6533 | -256.0996 | -2048.4916 | 335.9269 | 281.8918 | 2442.6651 | 339.015 | 809.6669 | 3534.6089 | 369.8797 |  |  |  |  | -536.7089 | -4709.0206 | 1547.7946 | 635.9692 | 3445.153 | 1534.5315 | -939.5238 | -4229.4468 | 886.5565 | 992.753 | 4494.7722 | 923.0699 |  |  |  |  | 790.9459 | 5907.1684 | 1867.7717 | -696.7654 | -7172.5563 | 1890.6837 | 1270.9727 | 6853.4857 | 579.7894 | -1212.6495 | -6587.1307 | 553.7554 |  |  |  |  | 830.7849 | 5990.3988 | 1854.0413 | -732.4202 | -7256.1002 | 1911.5512 | 1229.1881 | 6809.3629 | 562.5459 | -1175.0659 | -6541.716 | 563.7974 |  |  |  |  | 1129.7179 | 11860.7829 | 2551.1057 | -1048.1737 | -13334.49 | 2622.142 | 1660.0822 | 12956.8902 | -132.1282 | -1589.1428 | -12481.5606 | -149.1194 |  |  |  |  | 953.0061 | 5390.517 | 1755.6428 | -854.2217 | -6864.5875 | 1783.7355 | 1306.9323 | 6776.2089 | 681.5654 | -1253.25 | -6300.6669 | 671.0716
Fy | Fz | 703.4756 | 821.6296 | 768.4744 | 1784.7166 | 2449.9245 | 295.0781 | 998.5537 | 998.5537 | 768.4744 | 2449.9245 | 390.41 | 998.5537 | 0 | 95.8009 | -37.4562 | 0 | FIXED | -32.5837 | -18.8302 | -5.8042 | -41.6606 | 824.6453 | -17.9196 | -50.3799 | 760.6 | 4.9077 | -58.6037 | -105.618 | -6.6049 | -35.0456 | 24.0283 | 6.4486 | -45.1743 | -1171.6603 | 22.8338 | -57.1244 | -1237.1519 | -9.0168 | -69.8374 | -74.5524 | 5.1548 |  |  |  |  | -69.4812 | 784.029 | -41.1426 | -103.2165 | 676.1992 | 26.2598 | -87.3686 | -1168.976 | 53.4873 | -130.3387 | -1289.796 | -38.6084 |  |  |  |  | -109.386 | 650.0551 | 13.0987 | -67.7096 | 810.7227 | -45.0026 | -134.6795 | -1329.0105 | -23.4967 | -78.6314 | -1130.3109 | 55.4007 |  |  |  |  | -113.3165 | 635.8416 | 8.0707 | -68.6509 | 824.5505 | -40.7499 | -130.2176 | -1315.1666 | -51.441 | -78.2172 | -1143.7692 | 84.1205 |  |  |  |  | -122.646 | 827.0035 | -11.2449 | -64.4193 | 1168.9835 | -55.6143 | -139.0522 | -1669.0569 | 2.9492 | -64.2886 | -1325.4642 | 63.91 |  |  |  |  | -114.7508 | 919.3857 | 16.5259 | -66.5967 | 1076.5195 | -43.6606 | -133.803 | -1590.1334 | -23.1575 | -75.2513 | -1404.3158 | 50.2918
Fz | -Fy | -4892 | 1068.5604 | 626.141 | 873.4588 | 1340.1236 | 0 | -4892 | 0 | 626.141 | 1340.1236 | -720.04 | 768.4744 | 626.141 | 0 | 0 | 0 | GUIDED (min) | 65.0491 | 553.5583 | -78.7664 | 82.5276 | -1648.0687 | -50.3162 | 100.3229 | -2361.9293 | -103.0096 | 120.192 | -543.4543 | -80.7578 | 115.6026 | 485.3517 | -78.8095 | 97.1894 | 2032.5763 | -101.7362 | 78.7389 | 1324.0958 | -53.0896 | 60.4168 | -610.6474 | -79.6489 |  |  |  |  | 157.7242 | -1331.67 | -77.3584 | 218.75 | -2667.1133 | -236.2535 | 202.0859 | 2281.4263 | -224.2736 | 141.4734 | 948.8904 | -88.242 |  |  |  |  | 224.8153 | -3066.1141 | -224.5053 | 146.6338 | -933.3295 | -88.8423 | 135.3984 | 585.8787 | -97.8257 | 213.1852 | 2645.1609 | -214.9677 |  |  |  |  | 220.3022 | -3042.7563 | -259.5779 | 149.3861 | -958.4325 | -53.5842 | 139.3929 | 556.8005 | -87.7871 | 210.9444 | 2675.859 | -225.1856 |  |  |  |  | 224.295 | -4483.7635 | -206.0571 | 142.2462 | -501.5253 | -106.8937 | 135.8167 | 98.2595 | -111.9891 | 217.6755 | 4118.5626 | -201.2012 |  |  |  |  | 214.9512 | -3499.7355 | -222.8546 | 155.9485 | -1486.9351 | -90.5396 | 145.1943 | 1113.6551 | -97.797 | 203.9323 | 3104.5487 | -214.9499
Mx | Mx | 421.428 | 0 | 0 | 0 | 0 | 1240.3329 | 1661.7609 | 95.8009 | 0 | 0
My | Mz | 229.378 | 0 | 0 | 0 | 0 | 1299.1258 | 1528.5038 | -37.4562 | 0 | 0 | 2552.64 | 2449.9245 | 1340.1236 | 0 | 0 | 0 | GUIDED (max) | -367.7291 | 944.8122 | -166.3649 | -331.3368 | 6797.4795 | -248.0528 | -292.2622 | 5253.4288 | -82.6125 | -253.9976 | -1403.9783 | -170.8915 | -271.589 | 1176.2786 | -168.916 | -304.2206 | -6259.659 | -68.3346 | -344.1456 | -7804.6393 | -257.9351 | -387.3605 | -1153.5503 | -177.005 |  |  |  |  | -669.2976 | 7225.8205 | -573.5783 | -548.3122 | 4362.1898 | -89.4146 | -603.7132 | -5595.6494 | -59.5216 | -731.289 | -8442.2608 | -617.6211 |  |  |  |  | -528.5681 | 3591.4104 | -123.1726 | -698.5777 | 7999.7623 | -544.1233 | -750.043 | -9302.4738 | -573.3719 | -575.426 | -4738.4649 | -99.4555 |  |  |  |  | -556.257 | 3513.983 | -90.0156 | -687.7819 | 8078.0596 | -582.6595 | -719.4483 | -9237.6668 | -688.6386 | -589.1018 | -4804.4098 | 21.2035 |  |  |  |  | -535.7551 | 3278.4245 | -171.2398 | -723.3825 | 11809.9349 | -499.7942 | -738.795 | -13067.6527 | -517.9004 | -554.6806 | -4470.6067 | -151.1893 |  |  |  |  | -557.2051 | 5414.1326 | -123.3535 | -687.816 | 9676.1243 | -551.8169 | -716.874 | -10923.6284 | -554.4706 | -590.6924 | -6616.5285 | -110.4826
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-Ehy to be in same direction at Lvac)
Load Case: | 1.279 D - 2 Ehy + (Lvac + Lalign) | [6 empty] | Fixed/Gated | Fixed | Guided
FEA | IFO | E1 | A | B | C | D | E2 |  |  | Min | Max | Fx | Fy | Fz | Mx | My | Mz |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 | Fx5 | Fy5 | Fz5 | Fx6 | Fy6 | Fz6 | Fx7 | Fy7 | Fz7 | Fx8 | Fy8 | Fz8 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
Fx | Fx | -1394.5 | 2231.4 | -1020.5 | 710.88 | -1379 | 851.6 | -542.9 | 0 | -1379 | 2231.4 | -542.9 | 998.5537 | -7559.78 | 1661.7609 | 1565.96 | 0 | FIXED/GATED | -270.7107 | -5702.8895 | 1208.2582 | -52.4762 | -5373.0125 | 1221.5605 | 191.2365 | 2219.3511 | 1183.5566 | 420.6378 | 5632.1513 | 1229.1783 | -858.4487 | -6019.5581 | 692.7027 | -252.6676 | -2562.9659 | 644.9834 | 374.4838 | 4967.0376 | 672.6664 | 990.8376 | 5841.3772 | 706.8143 |  |  |  |  | -333.3089 | -8532.2537 | 2253.8641 | 625.3735 | 5308.6714 | 2173.863 | -987.7986 | -6089.9181 | 1502.658 | 1238.6296 | 8314.9583 | 1629.3248 |  |  |  |  | 744.3247 | 9399.7341 | 2518.1904 | -456.5582 | -12625.5584 | 2604.7538 | 1562.8431 | 12291.047 | 1267.306 | -1307.6995 | -10064.5223 | 1169.5298 |  |  |  |  | 811.7681 | 9492.6451 | 2496.9687 | -516.1417 | -12718.7591 | 2636.6113 | 1492.657 | 12262.0926 | 1258.8703 | -1245.3942 | -10033.7663 | 1167.2384 |  |  |  |  | 1081.6708 | 19099.8267 | 3218.0049 | -802.8756 | -23068.4182 | 3356.5533 | 1968.0879 | 22766.3344 | 529.94 | -1703.9961 | -19796.1204 | 455.2818 |  |  |  |  | 951.4429 | 8405.4516 | 2403.5827 | -653.8604 | -12374.9037 | 2501.3369 | 1555.1216 | 12290.4331 | 1361.4527 | -1309.8381 | -9319.5089 | 1293.4233
Fy | Fz | 703.4756 | 821.6296 | 768.4744 | 1784.7166 | 2449.9245 | 295.0781 | 998.5537 | 998.5537 | 768.4744 | 2449.9245 | 0 | 998.5537 | -2667.78 | 95.8009 | 0 | 0 | FIXED | 116.625 | -2340.9719 | 335.5459 | 40.552 | -1695.9414 | 329.4453 | -34.4223 | 1296.5295 | 326.0323 | -110.3871 | 2240.9574 | 340.6176 | -117.4235 | -2332.4065 | 337.498 | -41.7424 | -1686.1346 | 331.8903 | 35.4676 | 1287.2206 | 324.6346 | 111.3333 | 2232.2159 | 342.0894 |  |  |  |  | 133.9188 | -3039.2041 | 664.9268 | -113.8122 | 2539.7176 | 665.5913 | -135.6434 | -3029.4473 | 669.5888 | 115.5379 | 2530.3901 | 667.6464 |  |  |  |  | -156.0072 | 4142.6208 | 663.5175 | 172.4977 | -4642.2794 | 669.0675 | 157.1908 | 4108.5507 | 664.02 | -173.6814 | -4607.7025 | 671.1752 |  |  |  |  | -132.3333 | 4138.0879 | 650.9982 | 147.6275 | -4638.1085 | 684.3102 | 133.2512 | 4137.5631 | 644.8834 | -148.5454 | -4635.8195 | 687.5615 |  |  |  |  | -170.693 | 8066.0473 | 655.6543 | 180.8787 | -8564.9447 | 678.797 | 168.9535 | 8140.3873 | 665.0174 | -179.1419 | -8640.024 | 668.3113 |  |  |  |  | -116.3141 | 3934.3202 | 664.4659 | 133.7646 | -4433.7968 | 673.9407 | 114.3862 | 3924.0907 | 656.7299 | -131.8394 | -4423.1579 | 672.6435
Fz | -Fy | -5166.98 | 1068.5604 | 626.141 | 873.4588 | 1340.1236 | -2392.8 | -7559.78 | -2667.78 | 626.141 | 1340.1236 | -1379 | 768.4744 | 626.141 | 0 | 0 | 0 | GUIDED (min) | 147.0831 | 586.6216 | -79.0774 | 164.6208 | -3336.9172 | -27.4628 | 182.258 | -4048.142 | -125.4571 | 202.9179 | -510.2236 | -81.1229 | 198.7172 | 457.6852 | -78.7274 | 179.3156 | 3713.6491 | -125.5128 | 160.931 | 3009.6496 | -30.1216 | 143.1558 | -640.8712 | -78.6517 |  |  |  |  | 321.2319 | -2985.9891 | -10.8957 | 383.8063 | -4320.5757 | -304.0275 | 367.4585 | 3935.7454 | -291.1844 | 306.4902 | 2602.3528 | -20.0133 |  |  |  |  | 388.4614 | -4733.0193 | -282.6947 | 310.7148 | -2574.9306 | -31.1925 | 301.6672 | 2252.7839 | -39.913 | 378.1427 | 4286.762 | -272.3407 |  |  |  |  | 386.6237 | -4689.1679 | -337.3351 | 312.4128 | -2621.3839 | 24.5421 | 302.3537 | 2203.278 | -9.9573 | 377.5822 | 4338.7446 | -303.3844 |  |  |  |  | 388.3431 | -6588.6135 | -250.0189 | 308.2316 | -2607.6932 | -62.7308 | 300.9916 | 2203.1754 | -67.7525 | 381.4205 | 6224.6647 | -245.6388 |  |  |  |  | 379.6187 | -5609.3959 | -280.3086 | 321.3277 | -3589.1493 | -32.3771 | 309.6904 | 3223.3156 | -42.7343 | 368.3362 | 5206.7629 | -270.7209
Mx | Mx | 421.428 | 0 | 0 | 0 | 0 | 1240.3329 | 1661.7609 | 95.8009 | 0 | 0
My | Mz | 283.36 | 0 | 0 | 0 | 0 | 1282.6 | 1565.96 | 0 | 0 | 0 | 2231.4 | 2449.9245 | 1340.1236 | 0 | 0 | 0 | GUIDED (max) | -327.7379 | 960.9304 | -166.5165 | -291.3167 | 5974.1735 | -236.9119 | -252.3192 | 4431.4078 | -93.5555 | -213.6691 | -1387.7785 | -171.0695 | -231.071 | 1162.7914 | -168.8759 | -264.1844 | -5440.1437 | -79.9256 | -304.0774 | -6982.9396 | -246.7383 | -347.0256 | -1168.2843 | -176.5189 |  |  |  |  | -589.5884 | 6419.3474 | -541.1781 | -467.848 | 3556.1344 | -122.4541 | -523.0948 | -4789.1764 | -92.1403 | -650.8441 | -7636.2054 | -584.3599 |  |  |  |  | -448.7913 | 2778.8017 | -151.5397 | -618.5889 | 7199.4892 | -516.0193 | -668.9877 | -8489.8651 | -545.1398 | -495.01 | -3938.1918 | -127.4246 |  |  |  |  | -475.176 | 2711.3649 | -127.9219 | -608.3072 | 7267.3784 | -544.5733 | -640.0056 | -8435.0166 | -650.697 | -507.8666 | -3993.7607 | -16.918 |  |  |  |  | -455.7824 | 2252.3197 | -192.671 | -642.4654 | 10783.1876 | -478.265 | -658.2729 | -12041.5158 | -496.3352 | -474.8557 | -3443.8915 | -172.8524 |  |  |  |  | -476.9305 | 4385.6827 | -151.3621 | -607.1944 | 8651.3044 | -523.463 | -636.6829 | -9895.1785 | -527.6278 | -510.5462 | -5591.7086 | -137.6708
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Case: | 0.821 D + 2 Ehx | [6 empty] | Fixed/Gated | Fixed | Guided
FEA | IFO | E1 | A | B | C | D | E2 |  |  | Min | Max | Fx | Fy | Fz | Mx | My | Mz |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 | Fx5 | Fy5 | Fz5 | Fx6 | Fy6 | Fz6 | Fx7 | Fy7 | Fz7 | Fx8 | Fy8 | Fz8 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
Fx | Fx | 275.04 | 321.24 | 300.46 | 697.78 | 957.86 | 115.37 | 390.41 | 390.41 | 300.46 | 957.86 | 390.41 | 640.9793 | 0 | 61.4954 | -37.4562 | 0 | FIXED/GATED | -32.9344 | -20.3223 | -5.8875 | -42.2822 | 887.6984 | -18.6747 | -51.5607 | 845.8943 | 5.5753 | -60.63 | -73.604 | -6.4313 | -34.6975 | 22.5355 | 6.3636 | -44.5535 | -1108.785 | 22.0438 | -55.9301 | -1151.753 | -8.3358 | -67.8213 | -42.6275 | 5.3459 |  |  |  |  | -72.5216 | 852.9317 | -43.305 | -108.0831 | 786.1588 | 28.3877 | -84.3422 | -1100.0325 | 51.3464 | -125.4586 | -1180.031 | -36.4331 |  |  |  |  | -113.657 | 771.9199 | 14.9566 | -69.574 | 867.6863 | -46.8613 | -130.4083 | -1207.7467 | -21.6182 | -76.7672 | -1072.8324 | 53.5229 |  |  |  |  | -116.7706 | 757.7055 | 15.8733 | -69.9618 | 881.8355 | -48.4872 | -126.8065 | -1193.7834 | -43.7798 | -76.8632 | -1086.7306 | 76.394 |  |  |  |  | -125.4019 | 977.4598 | -9.7812 | -64.6335 | 1197.1784 | -57.0975 | -136.2753 | -1517.9947 | 4.4801 | -64.0955 | -1297.6103 | 62.3986 |  |  |  |  | -118.2009 | 1039.6075 | 17.9964 | -68.2549 | 1135.1564 | -45.0958 | -130.3705 | -1470.1653 | -21.8114 | -73.5755 | -1345.5718 | 48.9104
Fy | Fz | 451.5664 | 527.4104 | 493.2896 | 1145.6234 | 1572.6255 | 189.4129 | 640.9793 | 640.9793 | 493.2896 | 1572.6255 | 390.41 | 640.9793 | 0 | 61.4954 | -37.4562 | 0 | FIXED | -32.9344 | -20.3223 | -5.8875 | -42.2822 | 887.6984 | -18.6747 | -51.5607 | 845.8943 | 5.5753 | -60.63 | -73.604 | -6.4313 | -34.6975 | 22.5355 | 6.3636 | -44.5535 | -1108.785 | 22.0438 | -55.9301 | -1151.753 | -8.3358 | -67.8213 | -42.6275 | 5.3459 |  |  |  |  | -72.5216 | 852.9317 | -43.305 | -108.0831 | 786.1588 | 28.3877 | -84.3422 | -1100.0325 | 51.3464 | -125.4586 | -1180.031 | -36.4331 |  |  |  |  | -113.657 | 771.9199 | 14.9566 | -69.574 | 867.6863 | -46.8613 | -130.4083 | -1207.7467 | -21.6182 | -76.7672 | -1072.8324 | 53.5229 |  |  |  |  | -116.7706 | 757.7055 | 15.8733 | -69.9618 | 881.8355 | -48.4872 | -126.8065 | -1193.7834 | -43.7798 | -76.8632 | -1086.7306 | 76.394 |  |  |  |  | -125.4019 | 977.4598 | -9.7812 | -64.6335 | 1197.1784 | -57.0975 | -136.2753 | -1517.9947 | 4.4801 | -64.0955 | -1297.6103 | 62.3986 |  |  |  |  | -118.2009 | 1039.6075 | 17.9964 | -68.2549 | 1135.1564 | -45.0958 | -130.3705 | -1470.1653 | -21.8114 | -73.5755 | -1345.5718 | 48.9104
Fz | -Fy | 0 | 184.5936 | 172.6514 | 400.9682 | 550.4189 | 0 | 0 | 0 | 172.6514 | 550.4189 | 300.46 | 493.2896 | 172.6514 | 0 | 0 | 0 | GUIDED (min) | -43.2491 | 115.5219 | -21.3835 | -38.7011 | 766.092 | -30.6163 | -33.6727 | 567.3245 | -11.9627 | -28.5652 | -187.0328 | -22.1016 | -31.996 | 142.7621 | -21.6988 | -36.102 | -770.7127 | -9.4534 | -41.2486 | -969.7373 | -32.5981 | -46.9254 | -157.4969 | -22.8357 |  |  |  |  | -77.2147 | 815.1891 | -69.9528 | -61.5627 | 446.2815 | -15.5008 | -72.6075 | -694.0002 | -9.4908 | -89.0715 | -1060.7552 | -77.7083 |  |  |  |  | -59.5207 | 346.3315 | -19.2954 | -81.3995 | 915.5314 | -66.6959 | -90.9866 | -1170.944 | -72.3036 | -68.5503 | -584.1862 | -14.3565 |  |  |  |  | 386.6237 | -4689.1679 | -337.3351 | 312.4128 | -2621.3839 | 24.5421 | 302.3537 | 2203.278 | -9.9573 | 377.5822 | 4338.7446 | -303.3844 |  |  |  |  | -61.2184 | 287.2424 | -24.6903 | -85.3037 | 1386.3598 | -61.7476 | -88.7997 | -1637.236 | -65.5647 | -65.135 | -529.651 | -20.6489 |  |  |  |  | -63.4263 | 562.1213 | -19.0984 | -80.202 | 1111.5854 | -67.8583 | -86.527 | -1360.7548 | -69.741 | -70.2985 | -806.2366 | -15.9538
Mx | Mx | 88.6269 | 0 | 0 | 0 | 0 | -27.1316 | 61.4954 | 61.4954 | 0 | 0
My | Mz | -53.982 | 0 | 0 | 0 | 0 | 16.5258 | -37.4562 | -37.4562 | 0 | 0 | 957.86 | 1572.6255 | 550.4189 | 0 | 0 | 0 | GUIDED (max) | -137.8776 | 368.2888 | -68.1713 | -123.3783 | 2442.2846 | -97.6052 | -107.3477 | 1808.6064 | -38.138 | -91.0647 | -596.2664 | -70.4606 | -102.0023 | 455.1302 | -69.1766 | -115.0923 | -2457.0159 | -30.1384 | -131.4998 | -3091.5133 | -103.9232 | -149.5978 | -502.1067 | -72.8011 |  |  |  |  | -246.1591 | 2598.8088 | -223.0105 | -196.2599 | 1422.718 | -49.4188 | -231.471 | -2212.4541 | -30.2587 | -283.9589 | -3381.6826 | -247.735 |  |  |  |  | -189.7497 | 1104.0731 | -61.5159 | -259.5003 | 2918.704 | -212.6274 | -290.0641 | -3732.9682 | -230.5049 | -218.5365 | -1862.3636 | -45.7706 |  |  |  |  | -201.7456 | 1075.0149 | -59.9715 | -256.3683 | 2947.4976 | -216.3483 | -276.9014 | -3709.0618 | -284.2683 | -222.8256 | -1886.1155 | 10.1748 |  |  |  |  | -195.162 | 915.6832 | -78.7146 | -271.947 | 4419.7101 | -196.8524 | -283.0925 | -5219.5125 | -209.0214 | -207.6484 | -1688.4907 | -65.8305 |  |  |  |  | -202.2011 | 1792.0073 | -60.8879 | -255.6826 | 3543.7192 | -216.3331 | -275.8468 | -4338.0801 | -222.3353 | -224.1098 | -2570.2562 | -50.8627
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Load Case: | 0.821 D + 2 Ehy | [6 empty] | Fixed/Gated | Fixed | Guided
FEA | IFO | E1 | A | B | C | D | E2 |  |  | Min | Max | Fx | Fy | Fz | Mx | My | Mz |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 | Fx5 | Fy5 | Fz5 | Fx6 | Fy6 | Fz6 | Fx7 | Fy7 | Fz7 | Fx8 | Fy8 | Fz8 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  |  |  |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
Fx | Fx | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 640.9793 | 2667.78 | 61.4954 | 0 | 0 | FIXED/GATED | -115.0169 | 2347.8134 | -335.1639 | -37.702 | 1406.8335 | -325.983 | 39.8364 | -1687.6171 | -329.0937 | 119.6781 | -2387.7469 | -341.4135 | 115.8272 | 2339.251 | -337.1085 | 38.8958 | 1397.8415 | -328.2682 | -40.9438 | -1678.7873 | -327.757 | -120.5775 | -2378.5967 | -342.9655 |  |  |  |  | -119.9783 | 2723.2747 | -655.0122 | 136.1262 | -3043.8989 | -675.348 | 121.7665 | 2713.3308 | -659.7726 | -137.9139 | -3033.6794 | -677.6206 |  |  |  |  | 175.5901 | -4701.3895 | -672.0361 | -163.9491 | 4381.0927 | -660.5453 | -176.7751 | -4664.564 | -672.6334 | 165.134 | 4344.1546 | -662.5651 |  |  |  |  | 148.171 | -4696.8527 | -686.7741 | -141.6169 | 4375.4476 | -648.8336 | -148.8915 | -4694.1234 | -680.0115 | 142.3373 | 4374.2888 | -652.1342 |  |  |  |  | 183.3293 | -8755.9127 | -662.3659 | -179.8966 | 8435.6666 | -671.996 | -181.6863 | -8833.0304 | -672.0369 | 178.2563 | 8512.3097 | -661.3811 |  |  |  |  | 132.133 | -4485.5553 | -671.2083 | -126.1614 | 4164.9375 | -667.3603 | -130.1248 | -4474.1627 | -662.902 | 124.1558 | 4153.8077 | -666.3095
Fy | Fz | 451.5664 | 527.4104 | 493.2896 | 1145.6234 | 1572.6255 | 189.4129 | 640.9793 | 640.9793 | 493.2896 | 1572.6255 | 0 | 640.9793 | 2667.78 | 61.4954 | 0 | 0 | FIXED | -115.0169 | 2347.8134 | -335.1639 | -37.702 | 1406.8335 | -325.983 | 39.8364 | -1687.6171 | -329.0937 | 119.6781 | -2387.7469 | -341.4135 | 115.8272 | 2339.251 | -337.1085 | 38.8958 | 1397.8415 | -328.2682 | -40.9438 | -1678.7873 | -327.757 | -120.5775 | -2378.5967 | -342.9655 |  |  |  |  | -119.9783 | 2723.2747 | -655.0122 | 136.1262 | -3043.8989 | -675.348 | 121.7665 | 2713.3308 | -659.7726 | -137.9139 | -3033.6794 | -677.6206 |  |  |  |  | 175.5901 | -4701.3895 | -672.0361 | -163.9491 | 4381.0927 | -660.5453 | -176.7751 | -4664.564 | -672.6334 | 165.134 | 4344.1546 | -662.5651 |  |  |  |  | 148.171 | -4696.8527 | -686.7741 | -141.6169 | 4375.4476 | -648.8336 | -148.8915 | -4694.1234 | -680.0115 | 142.3373 | 4374.2888 | -652.1342 |  |  |  |  | 183.3293 | -8755.9127 | -662.3659 | -179.8966 | 8435.6666 | -671.996 | -181.6863 | -8833.0304 | -672.0369 | 178.2563 | 8512.3097 | -661.3811 |  |  |  |  | 132.133 | -4485.5553 | -671.2083 | -126.1614 | 4164.9375 | -667.3603 | -130.1248 | -4474.1627 | -662.902 | 124.1558 | 4153.8077 | -666.3095
Fz | -Fy | 274.98 | 184.5936 | 172.6514 | 400.9682 | 550.4189 | 2392.8 | 2667.78 | 2667.78 | 172.6514 | 550.4189 | 0 | 493.2896 | 172.6514 | 0 | 0 | 0 | GUIDED (min) | -5.8449 | 130.5974 | -21.5253 | -1.2698 | -3.9569 | -20.196 | 3.6865 | -201.5226 | -22.1978 | 9.1545 | -171.8809 | -22.2681 | 5.901 | 130.1473 | -21.6613 | 1.3443 | -4.2092 | -20.2946 | -3.7722 | -201.1906 | -22.1255 | -9.1997 | -171.2778 | -22.3811 |  |  |  |  | -2.6616 | 60.8843 | -39.6485 | 13.6965 | -307.6327 | -46.4031 | 2.7959 | 60.3047 | -39.9995 | -13.8303 | -306.841 | -46.5987 |  |  |  |  | 15.0956 | -413.7122 | -45.8275 | -6.585 | 167.0254 | -40.4098 | -15.1745 | -410.9004 | -45.8976 | 6.6638 | 164.3197 | -40.5163 |  |  |  |  | 12.5526 | -413.4828 | -54.2651 | -6.0833 | 166.3225 | -32.2407 | -12.554 | -412.7157 | -53.6805 | 6.0846 | 166.574 | -32.4634 |  |  |  |  | 13.5812 | -672.487 | -44.7352 | -9.6208 | 426.0296 | -41.6111 | -13.4864 | -677.4766 | -45.3945 | 9.5263 | 430.6493 | -40.9107 |  |  |  |  | 11.6556 | -399.8014 | -45.2952 | -4.7956 | 153.0579 | -41.3385 | -11.5231 | -398.8321 | -44.6345 | 4.6633 | 152.2908 | -41.3832
Mx | Mx | 88.6269 | 0 | 0 | 0 | 0 | -27.1316 | 61.4954 | 61.4954 | 0 | 0
My | Mz | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1572.6255 | 550.4189 | 0 | 0 | 0 | GUIDED (max) | -18.6336 | 416.3495 | -68.6234 | -4.0481 | -12.6148 | -64.3856 | 11.7526 | -642.4616 | -70.7675 | 29.185 | -547.9625 | -70.9914 | 18.8126 | 414.9144 | -69.0571 | 4.2858 | -13.4192 | -64.6999 | -12.0259 | -641.4032 | -70.537 | -29.3289 | -546.0399 | -71.3516 |  |  |  |  | -8.4853 | 194.1013 | -126.4007 | 43.6649 | -980.7443 | -147.9347 | 8.9136 | 192.2535 | -127.5198 | -44.0916 | -978.2202 | -148.5582 |  |  |  |  | 48.1252 | -1318.9296 | -146.0997 | -20.9931 | 532.4831 | -128.8281 | -48.3769 | -1309.9656 | -146.3234 | 21.2446 | 523.8573 | -129.1676 |  |  |  |  | 40.0183 | -1318.1983 | -172.999 | -19.3937 | 530.2421 | -102.7844 | -40.0226 | -1315.7529 | -171.1355 | 19.398 | 531.0442 | -103.4945 |  |  |  |  | 43.2972 | -2143.9132 | -142.6173 | -30.6716 | 1358.198 | -132.6576 | -42.9953 | -2159.8203 | -144.7193 | 30.3702 | 1372.9257 | -130.4248 |  |  |  |  | 37.1585 | -1274.5815 | -144.4027 | -15.2885 | 487.9542 | -131.7885 | -36.7362 | -1271.4913 | -142.2965 | 14.8667 | 485.5088 | -131.9312
Mz | -My | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | vert | shear |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 | Fx5 | Fy5 | Fz5 | Fx6 | Fy6 | Fz6 | Fx7 | Fy7 | Fz7 | Fx8 | Fy8 | Fz8 |  | vert | shear |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  | vert | shear |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  | vert | shear |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  | vert | shear |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 |  | vert | shear |  | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
[15 empty] | MAX | 5841.3772 | 2002.1164 | FIXED/GATED | 1.0721 | 2347.8134 | 1396.558 | 1.9001 | 1406.8335 | 1429.3627 | 364.1478 | 2219.3511 | 1370.2896 | 854.949 | 5632.1513 | 1421.2423 | 115.8272 | 2339.251 | 692.7027 | 38.8958 | 1397.8415 | 644.9834 | 539.2967 | 5663.9548 | 672.6664 | 1401.9245 | 5841.3772 | 706.8143 | MAX | 8967.7152 | 3110.5233 | FIXED/GATED | 9.2937 | 2723.2747 | 2547.9651 | 1195.4479 | 5308.6714 | 2407.6594 | 121.7665 | 2713.3308 | 1502.658 | 1784.1605 | 8967.7152 | 1629.3248 | MAX | 12774.2721 | 3824.943 | FIXED/GATED | 1451.7213 | 9399.7341 | 2962.6089 | 5.6991 | 4381.0927 | 3101.9679 | 2237.8526 | 12774.2721 | 1267.306 | 165.134 | 4344.1546 | 1169.5298 | MAX | 12681.2127 | 3817.9168 | FIXED/GATED | 1519.6124 | 9492.6451 | 2933.1095 | 4.0071 | 4375.4476 | 3143.9542 | 2166.1119 | 12681.2127 | 1258.8703 | 142.3373 | 4374.2888 | 1167.2384 | MAX | 23005.7193 | 5160.8211 | FIXED/GATED | 2011.0029 | 19099.8267 | 4095.9257 | 0.65474 | 8435.6666 | 4288.2963 | 2871.3392 | 23005.7193 | 529.94 | 178.2563 | 8512.3097 | 455.2818 | MAX | 13071.8209 | 3720.6537 | FIXED/GATED | 1717.4505 | 8405.4516 | 2778.7341 | 5.0688 | 4164.9375 | 2927.5941 | 2296.1832 | 13071.8209 | 1361.4527 | 124.1558 | 4153.8077 | 1293.4233
[15 empty] | MIN | -6048.5182 | 1235.1244 |  | -618.8182 | -5702.8895 | -335.1639 | -147.2166 | -6048.5182 | -325.983 | -51.5607 | -1687.6171 | -329.0937 | -60.63 | -2387.7469 | -341.4135 | -1186.5525 | -6019.5581 | -337.1085 | -339.107 | -2562.9659 | -328.2682 | -55.9301 | -1678.7873 | -327.757 | -120.5775 | -2378.5967 | -342.9655 | MIN | -8969.4105 | 1529.6558 |  | -739.5983 | -8969.4105 | -655.0122 | -108.0831 | -3043.8989 | -675.348 | -1371.3778 | -6089.9181 | -659.7726 | -137.9139 | -3033.6794 | -677.6206 | MIN | -12922.4959 | 1939.6742 |  | -113.657 | -4701.3895 | -672.0361 | -1001.6044 | -12922.4959 | -660.5453 | -176.7751 | -4664.564 | -672.6334 | -1819.3132 | -10064.5223 | -662.5651 | MIN | -13079.1329 | 1887.856 |  | -116.7706 | -4696.8527 | -686.7741 | -1058.5961 | -13079.1329 | -648.8336 | -148.8915 | -4694.1234 | -680.0115 | -1758.5055 | -10033.7663 | -652.1342 | MIN | -23279.4308 | 2531.1193 |  | -125.4019 | -8755.9127 | -662.3659 | -1573.4458 | -23279.4308 | -671.996 | -181.6863 | -8833.0304 | -672.0369 | -2440.2728 | -19796.1204 | -661.3811 | MIN | -12859.405 | 2004.8825 |  | -118.2009 | -4485.5553 | -671.2083 | -1255.8554 | -12859.405 | -667.3603 | -130.3705 | -4474.1627 | -662.902 | -1889.1886 | -9319.5089 | -666.3095
[15 empty] | MAX | 2347.8134 | 362.4196 | FIXED | 116.625 | 2347.8134 | 335.5459 | 40.552 | 1406.8335 | 329.4453 | 39.8364 | 1296.5295 | 326.0323 | 119.6781 | 2240.9574 | 340.6176 | 115.8272 | 2339.251 | 337.498 | 38.8958 | 1397.8415 | 331.8903 | 35.4676 | 1287.2206 | 324.6346 | 111.3333 | 2232.2159 | 342.0894 | MAX | 2723.2747 | 683.2858 | FIXED | 133.9188 | 2723.2747 | 664.9268 | 136.1262 | 2539.7176 | 665.5913 | 121.7665 | 2713.3308 | 669.5888 | 115.5379 | 2530.3901 | 667.6464 | MAX | 4381.0927 | 693.7636 | FIXED | 175.5901 | 4142.6208 | 663.5175 | 172.4977 | 4381.0927 | 669.0675 | 157.1908 | 4108.5507 | 664.02 | 165.134 | 4344.1546 | 671.1752 | MAX | 4375.4476 | 703.3459 | FIXED | 148.171 | 4138.0879 | 650.9982 | 147.6275 | 4375.4476 | 684.3102 | 133.2512 | 4137.5631 | 644.8834 | 142.3373 | 4374.2888 | 687.5615 | MAX | 8512.3097 | 703.118 | FIXED | 183.3293 | 8066.0473 | 655.6543 | 180.8787 | 8435.6666 | 678.797 | 168.9535 | 8140.3873 | 665.0174 | 178.2563 | 8512.3097 | 668.3113 | MAX | 4164.9375 | 687.0874 | FIXED | 132.133 | 3934.3202 | 664.4659 | 133.7646 | 4164.9375 | 673.9407 | 114.3862 | 3924.0907 | 656.7299 | 124.1558 | 4153.8077 | 672.6435
[15 empty] | MIN | -2387.7469 | 363.5441 |  | -115.0169 | -2340.9719 | -335.1639 | -42.2822 | -1695.9414 | -325.983 | -51.5607 | -1687.6171 | -329.0937 | -110.3871 | -2387.7469 | -341.4135 | -117.4235 | -2332.4065 | -337.1085 | -45.1743 | -1686.1346 | -328.2682 | -57.1244 | -1678.7873 | -327.757 | -120.5775 | -2378.5967 | -342.9655 | MIN | -3043.8989 | 691.5127 |  | -119.9783 | -3039.2041 | -655.0122 | -113.8122 | -3043.8989 | -675.348 | -135.6434 | -3029.4473 | -659.7726 | -137.9139 | -3033.6794 | -677.6206 | MIN | -4701.3895 | 695.4748 |  | -156.0072 | -4701.3895 | -672.0361 | -163.9491 | -4642.2794 | -660.5453 | -176.7751 | -4664.564 | -672.6334 | -173.6814 | -4607.7025 | -662.5651 | MIN | -4696.8527 | 702.7285 |  | -132.3333 | -4696.8527 | -686.7741 | -141.6169 | -4638.1085 | -648.8336 | -148.8915 | -4694.1234 | -680.0115 | -148.5454 | -4635.8195 | -652.1342 | MIN | -8833.0304 | 696.1635 |  | -170.693 | -8755.9127 | -662.3659 | -179.8966 | -8564.9447 | -671.996 | -181.6863 | -8833.0304 | -672.0369 | -179.1419 | -8640.024 | -661.3811 | MIN | -4485.5553 | 684.415 |  | -118.2009 | -4485.5553 | -671.2083 | -126.1614 | -4433.7968 | -667.3603 | -133.803 | -4474.1627 | -662.902 | -131.8394 | -4423.1579 | -666.3095
[15 empty] | MAX | 5946.1781 | 316.0244 | GUIDED (min) | 241.3586 | 803.9568 | -21.3835 | 264.7023 | 766.092 | -20.196 | 287.8122 | 567.3245 | -11.9627 | 315.2308 | -171.8809 | -22.1016 | 311.864 | 598.1226 | -21.6613 | 285.519 | 5946.1781 | -9.4534 | 261.3785 | 5022.8544 | -22.1255 | 238.5336 | -157.4969 | -22.3811 | MAX | 6235.0223 | 600.4277 | GUIDED (min) | 516.7151 | 815.1891 | 23.4419 | 599.9699 | 446.2815 | -15.5008 | 585.0512 | 6235.0223 | -9.4908 | 504.6425 | 4480.0984 | 16.019 | MAX | 6689.4158 | 606.2828 | GUIDED (min) | 605.9756 | 346.3315 | -19.2954 | 503.9324 | 915.5314 | -8.248 | 498.3115 | 4028.067 | -16.5432 | 598.1583 | 6689.4158 | -14.3565 | MIN | -7076.3936 | -483.7923 | GUIDED (min) | 12.5526 | -7076.3936 | -483.7923 | -10.3734 | -4365.6824 | -54.978 | -21.4076 | -703.7783 | -91.538 | 6.0846 | 166.574 | -451.9473 | MAX | 9515.4909 | 609.0417 | GUIDED (min) | 607.3477 | 287.2424 | -24.6903 | 503.089 | 1386.3598 | -41.6111 | 495.4903 | 4223.5169 | -45.3945 | 600.4517 | 9515.4909 | -20.6489 | MAX | 8173.8183 | 595.7934 | GUIDED (min) | 595.3737 | 562.1213 | -19.0984 | 519.0683 | 1111.5854 | -9.186 | 507.3844 | 5568.476 | -22.3595 | 584.5303 | 8173.8183 | -15.9538
[15 empty] | MIN | -6269.2699 | 185.9174 |  | -43.2491 | 115.5219 | -104.3327 | -38.7011 | -5334.9883 | -50.3162 | -33.6727 | -6269.2699 | -177.8467 | -28.5652 | -639.1592 | -106.8397 | -31.996 | 130.1473 | -103.6323 | -36.102 | -770.7127 | -179.898 | -41.2486 | -969.7373 | -53.0896 | -46.9254 | -848.8172 | -102.7693 | MIN | -6595.771 | 447.5583 |  | -77.2147 | -4840.3505 | -77.3584 | -61.5627 | -6595.771 | -438.6054 | -72.6075 | -694.0002 | -424.658 | -89.0715 | -1060.7552 | -88.242 | MIN | -7146.3194 | 415.1593 |  | -59.5207 | -7146.3194 | -405.0663 | -81.3995 | -4292.0818 | -88.8423 | -90.9866 | -1170.944 | -97.8257 | -68.5503 | -584.1862 | -393.9753 | [16 empty] | MIN | -9848.4893 | 364.8814 |  | -61.2184 | -9848.4893 | -353.9111 | -85.3037 | -4611.5192 | -106.8937 | -88.7997 | -1637.236 | -111.9891 | -65.135 | -529.651 | -350.8457 | MIN | -8562.8631 | 411.0085 |  | -63.4263 | -8562.8631 | -401.7973 | -80.202 | -5900.432 | -90.5396 | -86.527 | -1360.7548 | -97.797 | -70.2985 | -806.2366 | -390.49
[15 empty] | MAX | 9571.6827 | 86.9934 | GUIDED (max) | -18.6336 | 1108.2583 | -68.1713 | -4.0481 | 9571.6827 | -64.3856 | 20.041 | 7752.5904 | -38.138 | 49.7674 | -547.9625 | -70.4606 | 32.08 | 1432.7152 | -69.0571 | 7.3083 | -13.4192 | -30.1384 | -12.0259 | -641.4032 | -70.537 | -29.3289 | -502.1067 | -71.3516 | MAX | 10070.8495 | 166.1737 | GUIDED (max) | -8.4853 | 10070.8495 | -126.4007 | 74.459 | 6700.9015 | -43.4152 | 15.1997 | 327.8378 | -15.9596 | -44.0916 | -978.2202 | -148.5582 | MAX | 10970.2257 | 167.7653 | GUIDED (max) | 82.065 | 5805.8172 | -61.5159 | -20.9931 | 10970.2257 | -128.8281 | -48.3769 | -1309.9656 | -146.3234 | 36.2271 | 893.3011 | -45.7706 | MAX | 11081.1587 | 184.2394 | GUIDED (max) | 68.2407 | 5697.1644 | -26.3238 | -19.3937 | 11081.1587 | -102.7844 | -40.0226 | -1315.7529 | -171.1355 | 33.0782 | 905.5565 | 79.6275 | MAX | 15852.8824 | 162.4649 | GUIDED (max) | 73.832 | 5813.9527 | -78.7146 | -30.6716 | 15852.8824 | -132.6576 | -42.9953 | -2159.8203 | -144.7193 | 51.7885 | 2341.1643 | -65.8305 | MAX | 13339.0366 | 155.7668 | GUIDED (max) | 63.3641 | 8331.1067 | -60.8879 | -15.2885 | 13339.0366 | -131.7885 | -36.7362 | -1271.4913 | -142.2965 | 25.3513 | 827.9078 | -50.8627
[15 empty] | MIN | -10511.4565 | 615.9171 |  | -505.1705 | 368.2888 | -195.68 | -461.9334 | -21.5113 | -312.6815 | -415.8269 | -1095.5495 | -120.6754 | -371.9585 | -1655.5303 | -200.5236 | -389.1082 | 414.9144 | -199.0079 | -427.1135 | -8690.3955 | -110.3286 | -474.1258 | -10511.4565 | -322.062 | -525.0047 | -1306.3216 | -208.8711 | MIN | 194.1013 | 1266.1167 |  | -934.5936 | 194.1013 | -735.5736 | -793.5726 | -1672.402 | -252.2638 | -846.141 | -7860.8837 | -217.4515 | -995.8948 | -11209.4444 | -781.8216 | MIN | 532.4831 | 1249.7254 |  | -767.6803 | -2249.0882 | -249.1348 | -968.0996 | 532.4831 | -692.8172 | -1020.5068 | -12233.291 | -721.3733 | -813.9179 | -6841.1712 | -220.2614 | [16 empty] | MIN | 1358.198 | 1197.4344 |  | -773.8885 | -3655.8812 | -243.1964 | -996.324 | 1358.198 | -628.4623 | -1008.9113 | -17039.7847 | -644.9397 | -791.0789 | -6925.6275 | -222.4052 | MIN | 487.9542 | 1205.9665 |  | -801.3969 | -2173.4642 | -246.2409 | -955.7496 | 487.9542 | -701.6749 | -980.8198 | -14521.4571 | -697.5056 | -832.2007 | -9447.2632 | -224.974

## support matrix 17x36,8,xy
FEA: | FCT support concept 1 reaction matrix
CAD: | FEA FCT support concept 1
6" OD x 1/4" thick, telescoping support
baseplate: 1" thick, 17" x 36"
Triangular bracing to 26" height
8 bolts
1 kN, or 1 kNm applied
|  | FEA axes (not IFO) | [5 empty] | y=0
[8 empty] | FEA | FEA | TRANSPOSED for matrix multiplication:
anchor | Fanchor | Fx | Fy | Fz | Mx | My | Mz | x (m) | z (m) | Fanchor | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4 | Fx5 | Fy5 | Fz5 | Fx6 | Fy6 | Fz6 | Fx7 | Fy7 | Fz7 | Fx8 | Fy8 | Fz8
1 | Fx1 | -124.49 | 3.3234 | -43.349 | -24.417 | -401.51 | 1.188 | 0.1778 | -0.4191 | Fx | -124.49 | -50.175 | 0.47195 | -124.58 | 2562.9 | -34.681 | -124.34 | 2558.9 | 34.065 | -125.54 | -50.429 | 0.55411 | -126.13 | 41.985 | -0.12469 | -124.63 | -2551.1 | 36.082 | -124.73 | -2557.9 | -34.855 | -125.56 | 45.866 | -1.5132
| Fy1 | -50.175 | -42.923 | 879.06 | 490.89 | 90.992 | 34.513 | 0.1778 | -0.4191 | Fy | 3.3234 | -42.923 | 0.35532 | 2.5184 | -207.42 | 2.0035 | 2.5246 | -207.18 | -1.9811 | 3.3335 | -42.706 | -0.39094 | -3.3153 | -42.712 | 0.33501 | -2.5237 | -206.71 | 2.1117 | -2.5563 | -207.69 | -2.013 | -3.3046 | -42.663 | -0.42052
| Fz1 | 0.47195 | 0.35532 | -125.69 | -1.2754 | 166.09 | -1.1636 | 0.1778 | -0.4191 | Fz | -43.349 | 879.06 | -125.69 | -14.55 | 569.71 | -122.7 | 14.139 | -575.28 | -122.91 | 43.499 | -873.52 | -127.86 | 43.651 | 875.85 | -126.42 | 14.997 | 566.22 | -123.58 | -14.545 | -571.9 | -122.4 | -43.843 | -870.15 | -128.43
2 | Fx2 | -124.58 | 2.5184 | -14.55 | -8.1306 | -139.92 | -1.3149 | 0.1778 | -0.1397 | Mx | -24.417 | 490.89 | -1.2754 | -8.1306 | 324 | 1.1285 | 8.105 | -326.83 | 1.1867 | 24.321 | -488.07 | -0.98538 | 24.408 | 488.71 | -1.0158 | 8.2084 | 321.78 | 1.0168 | -8.1695 | -324.56 | 1.1314 | -24.325 | -485.92 | -1.1869
| Fy2 | 2562.9 | -207.42 | 569.71 | 324 | -3.8458 | -1442.3 | 0.1778 | -0.1397 | My | -401.51 | 90.992 | 166.09 | -139.92 | -3.8458 | 173.23 | 137.06 | 6.1185 | 174.26 | 407.15 | -92.688 | 169.17 | -404.98 | -92.595 | -167.13 | -139.26 | 2.7013 | -174.63 | 135.98 | 1.0513 | -173.34 | 405.47 | 88.265 | -167.64
| Fz2 | -34.681 | 2.0035 | -122.7 | 1.1285 | 173.23 | 19.061 | 0.1778 | -0.1397 | Mz | 1.188 | 34.513 | -1.1636 | -1.3149 | -1442.3 | 19.061 | -1.35 | -1439.5 | -18.516 | 1.0013 | 34.773 | 1.1968 | 1.46 | -29.285 | 1.2825 | -1.1256 | 1435 | -19.615 | -0.97873 | 1438.5 | 18.738 | 1.12 | -31.663 | -0.98421
3 | Fx3 | -124.34 | 2.5246 | 14.139 | 8.105 | 137.06 | -1.35 | 0.1778 | 0.1397
| Fy3 | 2558.9 | -207.18 | -575.28 | -326.83 | 6.1185 | -1439.5 | 0.1778 | 0.1397
| Fz3 | 34.065 | -1.9811 | -122.91 | 1.1867 | 174.26 | -18.516 | 0.1778 | 0.1397
4 | Fx4 | -125.54 | 3.3335 | 43.499 | 24.321 | 407.15 | 1.0013 | 0.1778 | 0.4191
| Fy4 | -50.429 | -42.706 | -873.52 | -488.07 | -92.688 | 34.773 | 0.1778 | 0.4191
| Fz4 | 0.55411 | -0.39094 | -127.86 | -0.98538 | 169.17 | 1.1968 | 0.1778 | 0.4191
5 | Fx5 | -126.13 | -3.3153 | 43.651 | 24.408 | -404.98 | 1.46 | -0.1778 | -0.4191
| Fy5 | 41.985 | -42.712 | 875.85 | 488.71 | -92.595 | -29.285 | -0.1778 | -0.4191
| Fz5 | -0.12469 | 0.33501 | -126.42 | -1.0158 | -167.13 | 1.2825 | -0.1778 | -0.4191
6 | Fx6 | -124.63 | -2.5237 | 14.997 | 8.2084 | -139.26 | -1.1256 | -0.1778 | -0.1397
| Fy6 | -2551.1 | -206.71 | 566.22 | 321.78 | 2.7013 | 1435 | -0.1778 | -0.1397
| Fz6 | 36.082 | 2.1117 | -123.58 | 1.0168 | -174.63 | -19.615 | -0.1778 | -0.1397
7 | Fx7 | -124.73 | -2.5563 | -14.545 | -8.1695 | 135.98 | -0.97873 | -0.1778 | 0.1397
| Fy7 | -2557.9 | -207.69 | -571.9 | -324.56 | 1.0513 | 1438.5 | -0.1778 | 0.1397
| Fz7 | -34.855 | -2.013 | -122.4 | 1.1314 | -173.34 | 18.738 | -0.1778 | 0.1397
8 | Fx8 | -125.56 | -3.3046 | -43.843 | -24.325 | 405.47 | 1.12 | -0.1778 | 0.4191
| Fy8 | 45.866 | -42.663 | -870.15 | -485.92 | 88.265 | -31.663 | -0.1778 | 0.4191
| Fz8 | -1.5132 | -0.42052 | -128.43 | -1.1869 | -167.64 | -0.98421 | -0.1778 | 0.4191
| sum Fx | -1000 | 0 | -0.001 | 0.0003 | -0.01 | 7e-05
| sum Fy | 0.047 | -1000.004 | -0.01 | 0 | -0.0007 | 0.038
| sum Fz | -0.00083 | -3e-05 | -999.99 | -8e-05 | 0.01 | -0.00051
| sum Mx | 0.011316 | 0.0081026 | -1785.2053 | -999.9642 | -0.020354 | -0.0075438
| sum My | -0.035645 | 0.0003335 | -0.092977 | 0.0015822 | 998.4983 | 0.0005729
| sum Mz | 1785.5289 | -0.080721 | -0.00889 | -0.003556 | 0.2052 | -1000.1367
| (F x height) = | 1788.16 | 0 | 1788.16

## support matrix 17x36,4,xy
FEA: | FCT support concept 1 reaction matrix
CAD: | FEA FCT support concept 1
6" OD x 1/4" thick, telescoping support
baseplate: 1" thick, 17" x 36"
Triangular bracing to 26" height, X & Y directions
4 bolts (in the corners)
1 kN, or 1 kNm applied
|  | FEA axes (not IFO) | [5 empty] | y=0
[8 empty] | FEA | FEA | TRANSPOSED for matrix multiplication:
anchor | Fanchor | Fx | Fy | Fz | Mx | My | Mz | x (m) | z (m) | Fanchor | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
1 | Fx1 | -248.13 | 11.06 | -47.016 | -26.655 | -504.61 | -0.062865 | 0.1778 | -0.4191 | Fx | -248.13 | 2510.5 | -100.86 | -250.48 | 2509.2 | 102.85 | -250.96 | -2510.5 | 101.54 | -250.42 | -2509.2 | -103.54
| Fy1 | 2510.5 | -250.06 | 1067.1 | 597.93 | 98.227 | -1406.4 | 0.1778 | -0.4191 | Fy | 11.06 | -250.06 | 6.0674 | 11.051 | -250.15 | -5.9666 | -11.019 | -249.94 | 5.9753 | -11.091 | -249.84 | -6.0761
| Fz1 | -100.86 | 6.0674 | -246.98 | -0.21023 | 208.36 | 55.491 | 0.1778 | -0.4191 | Fz | -47.016 | 1067.1 | -246.98 | 47.756 | -1067.1 | -251.72 | 47.677 | 1063.4 | -248.75 | -48.417 | -1063.4 | -252.54
2 | Fx2 | -250.48 | 11.051 | 47.756 | 26.673 | 507.71 | -0.1129 | 0.1778 | 0.4191 | Mx | -26.655 | 597.93 | -0.21023 | 26.673 | -597.93 | 0.16412 | 26.632 | 595.49 | 0.12342 | -26.65 | -595.49 | -0.077315
| Fy2 | 2509.2 | -250.15 | -1067.1 | -597.93 | -97.525 | -1405.4 | 0.1778 | 0.4191 | My | -504.61 | 98.227 | 208.36 | 507.71 | -97.525 | 212.29 | -508.87 | -98.203 | -210.02 | 505.77 | 97.502 | -210.63
| Fz2 | 102.85 | -5.9666 | -251.72 | 0.16412 | 212.29 | -55.282 | 0.1778 | 0.4191 | Mz | -0.062865 | -1406.4 | 55.491 | -0.1129 | -1405.4 | -55.282 | 0.14952 | 1406.4 | -55.215 | 0.026245 | 1405.5 | 55.007
3 | Fx3 | -250.96 | -11.019 | 47.677 | 26.632 | -508.87 | 0.14952 | -0.1778 | -0.4191
| Fy3 | -2510.5 | -249.94 | 1063.4 | 595.49 | -98.203 | 1406.4 | -0.1778 | -0.4191
| Fz3 | 101.54 | 5.9753 | -248.75 | 0.12342 | -210.02 | -55.215 | -0.1778 | -0.4191
4 | Fx4 | -250.42 | -11.091 | -48.417 | -26.65 | 505.77 | 0.026245 | -0.1778 | 0.4191
| Fy4 | -2509.2 | -249.84 | -1063.4 | -595.49 | 97.502 | 1405.5 | -0.1778 | 0.4191
| Fz4 | -103.54 | -6.0761 | -252.54 | -0.077315 | -210.63 | 55.007 | -0.1778 | 0.4191
| sum Fx | -999.99 | 0.001 | 0 | 0 | -5.6843e-14 | -1.7347e-17
| sum Fy | 0 | -999.99 | 0 | 0 | 0.001 | 0.1
| sum Fz | -0.01 | 0 | -999.99 | -5e-06 | -2.8422e-14 | 0.001
| sum Mx | 0 | 0.004191 | -1785.7851 | -1000.3246 | -0.019698 | 0.04191
| sum My | -0.049149 | 0.0018974 | -0.093548 | 0.0028828 | 999.0821 | 0.0015084
| sum Mz | 1785.0053 | -0.076454 | 0 | 0 | 0.24945 | -999.8939
| (F x height) = | 1788.16 | 0 | 1788.16

## support matrix 17x24,4,xy
FEA: | FCT support concept 2 reaction matrix
CAD: | FEA FCT support concept 2
6" OD x 1/4" thick, telescoping support
baseplate: 1" thick, 17" x 24"
Triangular bracing to 26" height, X & Y directions
4 bolts (in the corners)
1 kN, or 1 kNm applied
|  | FEA axes (not IFO) | [5 empty] | y=0
[8 empty] | FEA | FEA | TRANSPOSED for matrix multiplication:
anchor | Fanchor | Fx | Fy | Fz | Mx | My | Mz | x (m) | z (m) | Fanchor | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
1 | Fx1 | -248.34 | 8.5697 | 62.949 | 35.173 | 650.32 | -1.0497 | 0.1778 | -0.2667 | Fx | -248.34 | 2529.6 | 88.305 | -249 | 2491.2 | -87.486 | -252.32 | -2529.6 | -87.885 | -250.33 | -2491.2 | 87.066
| Fy1 | 2529.6 | -250.54 | -1680.4 | -940.9 | -74.505 | -1416.5 | 0.1778 | -0.2667 | Fy | 8.5697 | -250.54 | -5.1708 | 8.5987 | -249.58 | 5.1784 | -8.5743 | -249.53 | -5.2395 | -8.5942 | -250.34 | 5.232
| Fz1 | 88.305 | -5.1708 | -250.66 | -0.26007 | 432.19 | -48.834 | 0.1778 | -0.2667 | Fz | 62.949 | -1680.4 | -250.66 | -62.708 | 1680.5 | -248.85 | -63.393 | -1667 | -250.87 | 63.152 | 1667 | -249.62
2 | Fx2 | -249 | 8.5987 | -62.708 | -35.279 | -648.65 | -0.57595 | 0.1778 | 0.2667 | Mx | 35.173 | -940.9 | -0.26007 | -35.279 | 940.95 | 0.20363 | -35.134 | -933.91 | -0.14712 | 35.24 | 933.86 | 0.20356
| Fy2 | 2491.2 | -249.58 | 1680.5 | 940.95 | 74.529 | -1395.4 | 0.1778 | 0.2667 | My | 650.32 | -74.505 | 432.19 | -648.65 | 74.529 | 428.17 | 647.25 | 74.509 | -428.78 | -648.91 | -74.533 | -431.58
| Fz2 | -87.486 | 5.1784 | -248.85 | 0.20363 | 428.17 | 48.52 | 0.1778 | 0.2667 | Mz | -1.0497 | -1416.5 | -48.834 | -0.57595 | -1395.4 | 48.52 | 1.2633 | 1416.5 | 48.508 | 0.36229 | 1395.4 | -48.194
3 | Fx3 | -252.32 | -8.5743 | -63.393 | -35.134 | 647.25 | 1.2633 | -0.1778 | -0.2667
| Fy3 | -2529.6 | -249.53 | -1667 | -933.91 | 74.509 | 1416.5 | -0.1778 | -0.2667
| Fz3 | -87.885 | -5.2395 | -250.87 | -0.14712 | -428.78 | 48.508 | -0.1778 | -0.2667
4 | Fx4 | -250.33 | -8.5942 | 63.152 | 35.24 | -648.91 | 0.36229 | -0.1778 | 0.2667
| Fy4 | -2491.2 | -250.34 | 1667 | 933.86 | -74.533 | 1395.4 | -0.1778 | 0.2667
| Fz4 | 87.066 | 5.232 | -249.62 | 0.20356 | -431.58 | -48.194 | -0.1778 | 0.2667
| sum Fx | -999.99 | -0.0001 | 0 | 0 | 0.01 | -6e-05
| sum Fy | -4.5475e-13 | -999.99 | 0.1 | 1.1369e-13 | 0 | 0
| sum Fz | 0 | 0.0001 | -1000 | -2.7756e-17 | 5.6843e-14 | 0
| sum Mx | 0 | 0.040005 | 1785.5298 | 1000.0237 | -0.0021336 | 0
| sum My | 0.063475 | -0.00025781 | 0.062586 | -0.00073254 | -998.0652 | -0.0022918
| sum Mz | 1785.3965 | -0.04445 | 0.01778 | 0.01778 | 0.0085344 | -999.9116
| (F x height) = | 1788.16 | 0 | 1788.16

## support matrix 17x24,4,no
FEA: | FCT support concept 3 reaction matrix
CAD: | FEA FCT support concept 3
6" OD x 1/4" thick, telescoping support
baseplate: 1" thick, 17" x 24"
No bracing
4 bolts (in the corners)
1 kN, or 1 kNm applied
|  | FEA axes (not IFO) | [5 empty] | y=0
[8 empty] | FEA | FEA | TRANSPOSED for matrix multiplication:
anchor | Fanchor | Fx | Fy | Fz | Mx | My | Mz | x (m) | z (m) | Fanchor | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
1 | Fx1 | -252.4 | 6.8198 | 53.22 | 29.603 | 652.04 | 0.59427 | 0.1778 | -0.2667 | Fx | -252.4 | 2498.5 | 118 | -247.4 | 2523.6 | -118.56 | -247.3 | -2498.6 | -118.11 | -252.88 | -2523.5 | 118.67
| Fy1 | 2498.5 | -250.67 | -1678.7 | -939.52 | -19.13 | -1398.3 | 0.1778 | -0.2667 | Fy | 6.8198 | -250.67 | -21.74 | 6.5557 | -250.34 | 21.585 | -6.7179 | -249.36 | -21.409 | -6.6576 | -249.62 | 21.564
| Fz1 | 118 | -21.74 | -252.19 | -0.84205 | 432.73 | -65.204 | 0.1778 | -0.2667 | Fz | 53.22 | -1678.7 | -252.19 | -53.965 | 1678.6 | -248.41 | -53.519 | -1678 | -249.75 | 54.264 | 1678 | -249.64
2 | Fx2 | -247.4 | 6.5557 | -53.965 | -30.119 | -648.11 | -1.4763 | 0.1778 | 0.2667 | Mx | 29.603 | -939.52 | -0.84205 | -30.119 | 939.5 | 0.55516 | -29.41 | -939.16 | -0.17353 | 29.926 | 939.18 | 0.46042
| Fy2 | 2523.6 | -250.34 | 1678.6 | 939.5 | 19.096 | -1412.4 | 0.1778 | 0.2667 | My | 652.04 | -19.13 | 432.73 | -648.11 | 19.096 | 429.03 | 644.58 | 19.126 | -428.9 | -648.51 | -19.092 | -432.87
| Fz2 | -118.56 | 21.585 | -248.41 | 0.55516 | 429.03 | 65.717 | 0.1778 | 0.2667 | Mz | 0.59427 | -1398.3 | -65.204 | -1.4763 | -1412.4 | 65.717 | -0.93726 | 1398.4 | 65.276 | 1.8193 | 1412.4 | -65.789
3 | Fx3 | -247.3 | -6.7179 | -53.519 | -29.41 | 644.58 | -0.93726 | -0.1778 | -0.2667
| Fy3 | -2498.6 | -249.36 | -1678 | -939.16 | 19.126 | 1398.4 | -0.1778 | -0.2667
| Fz3 | -118.11 | -21.409 | -249.75 | -0.17353 | -428.9 | 65.276 | -0.1778 | -0.2667
4 | Fx4 | -252.88 | -6.6576 | 54.264 | 29.926 | -648.51 | 1.8193 | -0.1778 | 0.2667
| Fy4 | -2523.5 | -249.62 | 1678 | 939.18 | -19.092 | 1412.4 | -0.1778 | 0.2667
| Fz4 | 118.67 | 21.564 | -249.64 | 0.46042 | -432.87 | -65.789 | -0.1778 | 0.2667
| sum Fx | -999.98 | -1.7764e-15 | 0 | 0 | 0 | 1e-05
| sum Fy | 4.5475e-13 | -999.99 | -0.1 | 0 | 3.5527e-15 | 0.1
| sum Fz | 0 | 3.5527e-15 | -999.99 | 5.5511e-17 | -0.01 | 0
| sum Mx | 0.05334 | 0.018669 | 1790.4371 | 1002.0879 | 0.0021336 | -0.02667
| sum My | 0.04445 | 0.00076454 | 0.37462 | -0.00092812 | -998.0607 | 0.00053073
| sum Mz | 1785.8588 | -0.36093 | -0.01778 | -0.007112 | -0.01209 | -999.5027
| (F x height) = | 1788.16 | 0 | 1788.16

## support matrix 14x14,4,xy
FEA: | FCT support concept 4 reaction matrix
CAD: | FEA FCT support concept 4
6" OD x 1/4" thick, telescoping support
baseplate: 1" thick, 14" x 14"
bracing in x & y
4 bolts (in the corners)
1 kN, or 1 kNm applied
|  | FEA axes (not IFO) | [5 empty] | y=0
[8 empty] | FEA | FEA | TRANSPOSED for matrix multiplication:
anchor | Fanchor | Fx | Fy | Fz | Mx | My | Mz | x (m) | z (m) | Fanchor | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
1 | Fx1 | -248.95 | 4.128 | 66.868 | 37.307 | 885.02 | 0.071059 | 0.1397 | -0.1397 | Fx | -248.95 | 3194.2 | 66.714 | -251.89 | 3196.2 | -67.019 | -250.66 | -3194.3 | -67.131 | -248.49 | -3196.1 | 67.436
| Fy1 | 3194.2 | -249.92 | -3181 | -1780.8 | -3.1162 | -1788.4 | 0.1397 | -0.1397 | Fy | 4.128 | -249.92 | -4.1324 | 4.1485 | -249.7 | 4.1573 | -4.1565 | -250.06 | -4.216 | -4.12 | -250.31 | 4.1911
| Fz1 | 66.714 | -4.1324 | -247.3 | 0.40409 | 886.45 | -37.074 | 0.1397 | -0.1397 | Fz | 66.868 | -3181 | -247.3 | -67.577 | 3181 | -252.89 | -66.238 | -3209.5 | -250.88 | 66.948 | 3209.5 | -248.93
2 | Fx2 | -251.89 | 4.1485 | -67.577 | -36.997 | -889.65 | 0.27403 | 0.1397 | 0.1397 | Mx | 37.307 | -1780.8 | 0.40409 | -36.997 | 1780.8 | -0.096061 | -37.624 | -1797 | -0.68175 | 37.314 | 1797.1 | 0.37372
| Fy2 | 3196.2 | -249.7 | 3181 | 1780.8 | 2.8953 | -1789.3 | 0.1397 | 0.1397 | My | 885.02 | -3.1162 | 886.45 | -889.65 | 2.8953 | 896.82 | 892.7 | 3.1404 | -892.59 | -888.07 | -2.9195 | -890.68
| Fz2 | -67.019 | 4.1573 | -252.89 | -0.096061 | 896.82 | 36.941 | 0.1397 | 0.1397 | Mz | 0.071059 | -1788.4 | -37.074 | 0.27403 | -1789.3 | 36.941 | 0.056652 | 1788.4 | 37.867 | -0.40174 | 1789.3 | -37.734
3 | Fx3 | -250.66 | -4.1565 | -66.238 | -37.624 | 892.7 | 0.056652 | -0.1397 | -0.1397
| Fy3 | -3194.3 | -250.06 | -3209.5 | -1797 | 3.1404 | 1788.4 | -0.1397 | -0.1397
| Fz3 | -67.131 | -4.216 | -250.88 | -0.68175 | -892.59 | 37.867 | -0.1397 | -0.1397
4 | Fx4 | -248.49 | -4.12 | 66.948 | 37.314 | -888.07 | -0.40174 | -0.1397 | 0.1397
| Fy4 | -3196.1 | -250.31 | 3209.5 | 1797.1 | -2.9195 | 1789.3 | -0.1397 | 0.1397
| Fz4 | 67.436 | 4.1911 | -248.93 | 0.37372 | -890.68 | -37.734 | -0.1397 | 0.1397
| sum Fx | -999.99 | 0 | 0.001 | 0 | 0 | 1e-06
| sum Fy | -4.5475e-13 | -999.99 | 0 | 0.1 | 0 | 2.2737e-13
| sum Fz | 0 | 0 | -1000 | -1e-06 | 0 | 0
| sum Mx | 0.02794 | -0.004191 | 1785.5057 | 999.6513 | -0.0067615 | 0
| sum My | -0.022352 | 0.0010058 | -0.1228 | 0.0025064 | -994.9406 | 0.0014779
| sum Mz | 1785.4778 | 0.10478 | 0 | -0.01397 | -0.061719 | -999.6094
| (F x height) = | 1788.16 | 0 | 1788.16

## support matrix 25x14,4,xy
FEA: | FCT support concept 6 reaction matrix
CAD: | FEA FCT support concept 6
6" OD x 1/4" thick, telescoping support
baseplate: 1" thick, 14" x 25"
bracing in x & y
4 bolts (in the corners)
1 kN, or 1 kNm applied
|  | FEA axes (not IFO) | [5 empty] | y=0
[8 empty] | FEA | FEA | TRANSPOSED for matrix multiplication:
anchor | Fanchor | Fx | Fy | Fz | Mx | My | Mz | x (m) | z (m) | Fanchor | Fx1 | Fy1 | Fz1 | Fx2 | Fy2 | Fz2 | Fx3 | Fy3 | Fz3 | Fx4 | Fy4 | Fz4
1 | Fx1 | -249.89 | 7.1045 | 47.211 | 26.516 | 716.19 | -0.13574 | 0.1397 | -0.2794 | Fx | -249.89 | 3201.5 | 87.189 | -250.97 | 3190.2 | -88.264 | -249.63 | -3201.5 | -83.56 | -249.49 | -3190.2 | 84.635
| Fy1 | 3201.5 | -250.27 | -1600.6 | -895.82 | -139.27 | -1792.1 | 0.1397 | -0.2794 | Fy | 7.1045 | -250.27 | -4.1092 | 7.2201 | -249.93 | 4.0904 | -7.0953 | -249.74 | -3.8304 | -7.2293 | -250.05 | 3.8492
| Fz1 | 87.189 | -4.1092 | -250.61 | -0.033277 | 357.94 | -47.726 | 0.1397 | -0.2794 | Fz | 47.211 | -1600.6 | -250.61 | -48.405 | 1600.6 | -251.12 | -46.47 | -1596.5 | -247.58 | 47.665 | 1596.5 | -250.69
2 | Fx2 | -250.97 | 7.2201 | -48.405 | -26.92 | -714.27 | 0.49293 | 0.1397 | 0.2794 | Mx | 26.516 | -895.82 | -0.033277 | -26.92 | 895.82 | -0.80008 | -26.101 | -893.95 | 0.68625 | 26.505 | 893.95 | 0.14709
| Fy2 | 3190.2 | -249.93 | 1600.6 | 895.82 | 139.32 | -1786 | 0.1397 | 0.2794 | My | 716.19 | -139.27 | 357.94 | -714.27 | 139.32 | 352.66 | 714.42 | 139.25 | -353.06 | -716.35 | -139.29 | -357.53
| Fz2 | -88.264 | 4.0904 | -251.12 | -0.80008 | 352.66 | 48.107 | 0.1397 | 0.2794 | Mz | -0.13574 | -1792.1 | -47.726 | 0.49293 | -1786 | 48.107 | -0.049467 | 1792.1 | 46.045 | -0.30772 | 1786 | -46.426
3 | Fx3 | -249.63 | -7.0953 | -46.47 | -26.101 | 714.42 | -0.049467 | -0.1397 | -0.2794
| Fy3 | -3201.5 | -249.74 | -1596.5 | -893.95 | 139.25 | 1792.1 | -0.1397 | -0.2794
| Fz3 | -83.56 | -3.8304 | -247.58 | 0.68625 | -353.06 | 46.045 | -0.1397 | -0.2794
4 | Fx4 | -249.49 | -7.2293 | 47.665 | 26.505 | -716.35 | -0.30772 | -0.1397 | 0.2794
| Fy4 | -3190.2 | -250.05 | 1596.5 | 893.95 | -139.29 | 1786 | -0.1397 | 0.2794
| Fz4 | 84.635 | 3.8492 | -250.69 | 0.14709 | -357.53 | -46.426 | -0.1397 | 0.2794
| sum Fx | -999.98 | 0 | 0.001 | -3.5527e-15 | -0.01 | 3e-06
| sum Fy | 0 | -999.99 | 0 | 0 | 0.01 | 0
| sum Fz | 0 | -4.4409e-16 | -1000 | -1.7e-05 | 0.01 | 0
| sum Mx | 0 | 0.008382 | 1786.5395 | 1000.1235 | 0.01397 | 0
| sum My | 0.037719 | 0.00011176 | 0.069571 | 0.00093557 | -997.9679 | -0.0029569
| sum Mz | 1785.841 | -0.057277 | 0 | 0 | 0.012573 | -999.7211
| (F x height) = | 1788.16 | 0 | 1788.16

## Ansys solid model 2 subassys
FEA: | FCT beam approx 3
CAD: | NA
Single repeating section with assumed fixed boundary conditions at the Fixed Support (type E)
Floor Anchor Forces for individual loads:
Load Case: |  | D (dead load)
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [40 empty] | Fx | 0 | 0
Fy | Fz | [40 empty] | Fz | 0 | 0
Fz | -Fy | [40 empty] | -Fy | 0 | 0
Load Case: |  | Lvac (atmospheric-vacuum pressure load)
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [40 empty] | Fx | 0 | 0
Fy | Fz | [40 empty] | Fz | 0 | 0
Fz | -Fy | [40 empty] | -Fy | 0 | 0
Load Case: |  | Ehx (lateral earthquake)
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [40 empty] | Fx | 0 | 0
Fy | Fz | [40 empty] | Fz | 0 | 0
Fz | -Fy | [40 empty] | -Fy | 0 | 0
Load Case: |  | Ehy (axial earthquake)
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [40 empty] | Fx | 0 | 0
Fy | Fz | [40 empty] | Fz | 0 | 0
Fz | -Fy | [40 empty] | -Fy | 0 | 0
ASCE 7-16 LRFD Load Cases:
Linear superposition of the anchor loads from each of the above individual load cases, with the indicated load factors
Load Case: |  | 1.4 D (1.4 x dead load)
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [40 empty] | Fx | 0 | 0
Fy | Fz | [40 empty] | Fz | 0 | 0
Fz | -Fy | [40 empty] | -Fy | 0 | 0
Load Case: |  | 1.2 D + 1.6 Lvac
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [40 empty] | Fx | 0 | 0
Fy | Fz | [40 empty] | Fz | 0 | 0
Fz | -Fy | [40 empty] | -Fy | 0 | 0
Load Case: |  | 1.279 D + 2 Ehx + Lvac
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [40 empty] | Fx | 0 | 0
Fy | Fz | [40 empty] | Fz | 0 | 0
Fz | -Fy | [40 empty] | -Fy | 0 | 0
Load Case: |  | 1.279 D + 2 Ehy + Lvac
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [40 empty] | Fx | 0 | 0
Fy | Fz | [40 empty] | Fz | 0 | 0
Fz | -Fy | [40 empty] | -Fy | 0 | 0
Load Case: |  | 0.821 D + 2 Ehx
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [40 empty] | Fx | 0 | 0
Fy | Fz | [40 empty] | Fz | 0 | 0
Fz | -Fy | [40 empty] | -Fy | 0 | 0
Load Case: |  | 0.821 D + 2 Ehy
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [40 empty] | Fx | 0 | 0
Fy | Fz | [40 empty] | Fz | 0 | 0
Fz | -Fy | [40 empty] | -Fy | 0 | 0
Load Case: |  | 1.2 D + 1.6 Lvac |  | BRACED IN Y ONLY, .1" radial gap
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | -6768.7 | -2583.3 | 2274.3 | 6686.8 | -6813.3 | -2642.5 | 2168.6 | 6629.5 | -5546.1 | -2297.1 | 1993.9 | 5285.1 | -5659 | -2131.9 | 1508.3 | 5204.1 | -709.42 | -286.31 | 297.6 | 892.81 | -158.75 | -137.08 | 60.584 | 210.76 | -4662.7 | -1270 | 2390.6 | 5758.7 | -4795.6 | -1365.2 | 2460.9 | 5897.2 | [8 empty] | Fx | -6813.3 | 6686.8
Fy | Fz | 992.56 | 5400.4 | -779.11 | -1127.1 | -2736 | -6441.1 | 8.9247 | 2408.2 | 1388.9 | 6469 | 1100.3 | -1582.6 | -1685.9 | -6861.6 | -2559.7 | 1311.4 | 4679.6 | 2636.2 | -828.98 | -2444.2 | 4324.4 | 556.57 | -2134.2 | -2224.6 | 433.84 | -8846.9 | -13038 | -865.4 | -1950.1 | 7995.7 | 13069 | 2460.8 | [8 empty] | Fz | -13038 | 13069
Fz | -Fy | 3185.3 | 3386.5 | 3387.8 | 2750.1 | -3138.2 | -3412.2 | -3468.3 | -2723.7 | 2450 | 2753.7 | 2764.4 | 2294.2 | -2558.5 | -2681.2 | -2804.4 | -2244.3 | -182.64 | -138.39 | -140.8 | -152.92 | -637.37 | -580.34 | -663.73 | -544.57 | 2231.1 | 2656.9 | 2148.1 | 2183.6 | -2639.3 | -2765.2 | -2227.8 | -2139.3 | [8 empty] | -Fy | -3468.3 | 3387.8
Load Case: |  | 1.2 D + 1.6 Lvac |  | BRACED IN X & Y, .1" radial gap (point masses accidentily inactive)
FEA | IFO | C1 | C2 | C3 | C4 | C5 | C6 | C7 | C8 | D1 | D2 | D3 | D4 | D5 | D6 | D7 | D8 | E1 | E2 | E3 | E4 | E5 | E6 | E7 | E8 | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | B1 | B2 | B3 | B4 | B5 | B6 | B7 | B8 | IFO | Min | Max
Fx | Fx | [24 empty] | -4541.3 | -1177.3 | 2842.2 | [13 empty] | Fx | -4541.3 | 2842.2
Fy | Fz | [24 empty] | 1072 | -14547 | -13365 | [13 empty] | Fz | -14547 | 1072
Fz | -Fy | [24 empty] | 2597.4 | 2697.9 | 2281 | [13 empty] | -Fy | 2281 | 2697.9

## Anchor Resistance
The following is based on Hilti guidance:
https://www.hilti.com/medias/sys_master/documents/hbf/9175927062558/Product_Technical_Guide_Excerpt_for_ACI_318_Chapter_17_Strength_Design_-_SD_LRFD_Technical_information_ASSET_DOC_LOC_5941017.pdf
which is in turn based on ACI 318 Chapter 17
Data on the Hilti anchor rod specifications and technical data:
https://www.hilti.com/medias/sys_master/documents/h97/h6f/9485220511774/Technical-information-ASSET-DOC-LOC-3008312.pdf
These are only approximate calculations used to ascertain the reasonableness of the preliminary design.
Final calculations should be performed for example with Hilti PROFIS software:
https://www.hilti.com/content/hilti/W1/US/en/engineering/software/hilti-software/structural-engineering/profis-engineering-suite.html
Hilti simplified design calculation tables from:
https://www.hilti.com/content/hilti/W1/US/en/engineering/technical-information/technical-guides.html
Assuming cracked, 3,000 psi concrete
Use adhesive embedded anchors with minimum embedment depth (to minimize slab cost)
HAS-B-105
[5 empty] | concrete/adhesive bond |  |  |  | steel | [5 empty] | @11 in spacing |  | @min concrete
| Nominal | Effective | Drill | Concrete | Tension φNn | Tension φNn | Shear | Shear | Tension φNsa | Tension φNsa | Shear | Shear | Seismic | Seismic | Spacing factor | Spacing factor | Concrete | Tension | Tension | Shear | Shear
| Anchor | Embedment | Diameter | depth | (kN) | (lbf) | φVn | φVn | (kN) | (lbf) | φVsa | φVsa | Shear | Shear |  |  | thickness | min | min | min | min
| Dia. (in) | hef (in) | d0 (in) | min. (in) |  |  | (kN) | (lbf) |  |  | (kN) | (lbf) | φVsa,eq | φVsa,eq | in tension | in shear | factor in | allow | allow | allow | allow
[13 empty] | (kN) | (lbf) | ƒAN | ƒAV | shear, ƒHV | (kN) | (lbf) | (kN) | (lbf)
| 0.375 | 2.375 | 0.5 | 3.625 | 5 | 1120 | 6.3 | 1425 | 32.3 | 7270 | 16.8 | 3780 | 11.8 | 2645 | 1 | 1 | 0.84 | 5 | 1120 | 5.3 | 1197
| 0.375 | 3.375 | 0.5 | 4.625 | 7.1 | 1590 | 18 | 4055 | 32.3 | 7270 | 16.8 | 3780 | 11.8 | 2645 | 1 | 1 | 0.68 | 7.1 | 1590 | 8 | 1799
| 0.5 | 2.75 | 0.625 | 4 | 7.8 | 1760 | 16.9 | 3790 | 59.2 | 13305 | 30.8 | 6920 | 21.6 | 4845 | 1 | 0.81 | 0.66 | 7.8 | 1760 | 9 | 2026
--> | 0.5 | 4.5 | 0.625 | 5.75 | 12.8 | 2880 | 27.6 | 6200 | 59.2 | 13305 | 30.8 | 6920 | 21.6 | 4845 | 0.92 | 0.73 | 0.69 | 11.8 | 2650 | 10.9 | 2440
| 0.625 | 3.125 | 0.75 | 4.625 | 7.9 | 1785 | 20.2 | 4550 | 94.3 | 21190 | 49 | 11020 | 34.3 | 7715 | 0.91 | 0.78 | 0.69 | 7.2 | 1624 | 10.9 | 2449
| 0.625 | 5.625 | 0.75 | 7.125 | 14.3 | 3215 | 36.4 | 8190 | 94.3 | 21190 | 49 | 11020 | 34.3 | 7715 | 0.83 | 0.7 | 0.72 | 11.9 | 2668 | 17.3 | 3888
| 0.75 | 3.5 | 0.875 | 5.25 | 10.2 | 2295 | 22 | 4940 | 139.5 | 31360 | 72.6 | 16310 | 50.8 | 11415 | 0.85 | 0.77 | 0.73 | 8.7 | 1951 | 12.4 | 2777
| 0.75 | 6.75 | 0.875 | 8.5 | 19.7 | 4420 | 42.4 | 9525 | 139.5 | 31360 | 72.6 | 16310 | 50.8 | 11415 | 0.77 | 0.69 | 0.77 | 15.2 | 3403 | 22.5 | 5061

## anchor resistance (from -v3)
The following is based on Hilti guidance:
https://www.hilti.com/medias/sys_master/documents/hbf/9175927062558/Product_Technical_Guide_Excerpt_for_ACI_318_Chapter_17_Strength_Design_-_SD_LRFD_Technical_information_ASSET_DOC_LOC_5941017.pdf
which is in turn based on ACI 318 Chapter 17
Data on the Hilti anchor rod specifications and technical data:
https://www.hilti.com/medias/sys_master/documents/h97/h6f/9485220511774/Technical-information-ASSET-DOC-LOC-3008312.pdf
These are only approximate calculations used to ascertain the reasonableness of the preliminary design.
Final calculations should be performed for example with Hilti PROFIS software:
https://www.hilti.com/content/hilti/W1/US/en/engineering/software/hilti-software/structural-engineering/profis-engineering-suite.html
Hilti simplified design calculation tables from:
https://www.hilti.com/content/hilti/W1/US/en/engineering/technical-information/technical-guides.html
Assuming cracked, 3,000 psi concrete
Use adhesive embedded anchors with minimum embedment depth (to minimize slab cost)
HAS-B-105
[5 empty] | concrete/adhesive bond |  |  |  | steel | [5 empty] | @11 in spacing |  | @min concrete
| Nominal Anchor Dia. (in) | Effective Embedment hef (in) | Drill Diameter d0 (in) | Concrete depth min. (in) | Tension φNn (kN) | Tension φNn (lbf) | Shear φVn (kN) | Shear φVn (lbf) | Tension φNsa (kN) | Tension φNsa (lbf) | Shear φVsa (kN) | Shear φVsa (lbf) | Seismic Shear φVsa,eq (kN) | Seismic Shear φVsa,eq (lbf) | Spacing factor in tension ƒAN | Spacing factor in shear ƒAV | Concrete thickness factor in shear, ƒHV | Tension min allow (kN) | Tension min allow (lbf) | Shear min allow (kN) | Shear min allow (lbf)
| 0.375 | 2.375 | 0.5 | 3.625 | 5 | 1120 | 6.3 | 1425 | 32.3 | 7270 | 16.8 | 3780 | 11.8 | 2645 | 1 | 1 | 0.84 | 5 | 1120 | 5.292 | 1197
| 0.375 | 3.375 | 0.5 | 4.625 | 7.1 | 1590 | 18 | 4055 | 32.3 | 7270 | 16.8 | 3780 | 11.8 | 2645 | 1 | 1 | 0.68 | 7.1 | 1590 | 8.024 | 1798.6
| 0.5 | 2.75 | 0.625 | 4 | 7.8 | 1760 | 16.9 | 3790 | 59.2 | 13305 | 30.8 | 6920 | 21.6 | 4845 | 1 | 0.81 | 0.66 | 7.8 | 1760 | 9.0347 | 2026.134
--> | 0.5 | 4.5 | 0.625 | 5.75 | 12.8 | 2880 | 27.6 | 6200 | 59.2 | 13305 | 30.8 | 6920 | 21.6 | 4845 | 0.92 | 0.73 | 0.69 | 11.776 | 2649.6 | 10.8799 | 2440.4265
| 0.625 | 3.125 | 0.75 | 4.625 | 7.9 | 1785 | 20.2 | 4550 | 94.3 | 21190 | 49 | 11020 | 34.3 | 7715 | 0.91 | 0.78 | 0.69 | 7.189 | 1624.35 | 10.8716 | 2448.81
| 0.625 | 5.625 | 0.75 | 7.125 | 14.3 | 3215 | 36.4 | 8190 | 94.3 | 21190 | 49 | 11020 | 34.3 | 7715 | 0.83 | 0.7 | 0.72 | 11.869 | 2668.45 | 17.2872 | 3888.36
| 0.75 | 3.5 | 0.875 | 5.25 | 10.2 | 2295 | 22 | 4940 | 139.5 | 31360 | 72.6 | 16310 | 50.8 | 11415 | 0.85 | 0.77 | 0.73 | 8.67 | 1950.75 | 12.3662 | 2776.774
| 0.75 | 6.75 | 0.875 | 8.5 | 19.7 | 4420 | 42.4 | 9525 | 139.5 | 31360 | 72.6 | 16310 | 50.8 | 11415 | 0.77 | 0.69 | 0.77 | 15.169 | 3403.4 | 22.5271 | 5060.6325
0.5

## anchor resistance -v4 additions
The following is based on Hilti guidance:
https://www.hilti.com/medias/sys_master/documents/hbf/9175927062558/Product_Technical_Guide_Excerpt_for_ACI_318_Chapter_17_Strength_Design_-_SD_LRFD_Technical_information_ASSET_DOC_LOC_5941017.pdf
which is in turn based on ACI 318 Chapter 17
Data on the Hilti anchor rod specifications and technical data:
https://www.hilti.com/medias/sys_master/documents/h97/h6f/9485220511774/Technical-information-ASSET-DOC-LOC-3008312.pdf
These are only approximate calculations used to ascertain the reasonableness of the preliminary design.
Final calculations should be performed for example with Hilti PROFIS software:
https://www.hilti.com/content/hilti/W1/US/en/engineering/software/hilti-software/structural-engineering/profis-engineering-suite.html
Hilti simplified design calculation tables from:
https://www.hilti.com/content/hilti/W1/US/en/engineering/technical-information/technical-guides.html
| Assuming cracked, 3,000 psi concrete | [9 empty] | v4 updated calc to document HIT-RE strength
Use adhesive embedded anchors with minimum embedment depth (to minimize slab cost)
HAS-B-105
[5 empty] | concrete/adhesive bond |  |  |  | steel | [5 empty] | @11 in spacing |  | @min concrete
| Nominal Anchor Dia. (in) | Effective Embedment hef (in) | Drill Diameter d0 (in) | Concrete depth min. (in) | Tension φNn (kN) | Tension φNn (lbf) | Shear φVn (kN) | Shear φVn (lbf) | Tension φNsa (kN) | Tension φNsa (lbf) | Shear φVsa (kN) | Shear φVsa (lbf) | Seismic Shear φVsa,eq (kN) | Seismic Shear φVsa,eq (lbf) | Spacing factor in tension ƒAN | Spacing factor in shear ƒAV | Concrete thickness factor in shear, ƒHV | Tension min allow (kN) | Tension min allow (lbf) | Shear min allow (kN) | Shear min allow (lbf)
| 0.375 | 2.375 | 0.5 | 3.625 | 5 | 1120 | 6.3 | 1425 | 32.3 | 7270 | 16.8 | 3780 | 11.8 | 2645 | 1 | 1 | 0.84 | 5 | 1120 | 5.292 | 1197
| 0.375 | 3.375 | 0.5 | 4.625 | 7.1 | 1590 | 18 | 4055 | 32.3 | 7270 | 16.8 | 3780 | 11.8 | 2645 | 1 | 1 | 0.68 | 7.1 | 1590 | 8.024 | 1798.6
| 0.5 | 2.75 | 0.625 | 4 | 7.8 | 1760 | 16.9 | 3790 | 59.2 | 13305 | 30.8 | 6920 | 21.6 | 4845 | 1 | 0.81 | 0.66 | 7.8 | 1760 | 9.0347 | 2026.134
--> | 0.5 | 4.5 | 0.625 | 5.75 | 12.8 | 2880 | 27.6 | 6200 | 59.2 | 13305 | 30.8 | 6920 | 21.6 | 4845 | 0.92 | 0.73 | 0.69 | 11.776 | 2649.6 | 10.8799 | 2440.4265
| 0.625 | 3.125 | 0.75 | 4.625 | 7.9 | 1785 | 20.2 | 4550 | 94.3 | 21190 | 49 | 11020 | 34.3 | 7715 | 0.91 | 0.78 | 0.69 | 7.189 | 1624.35 | 10.8716 | 2448.81
| 0.625 | 5.625 | 0.75 | 7.125 | 14.3 | 3215 | 36.4 | 8190 | 94.3 | 21190 | 49 | 11020 | 34.3 | 7715 | 0.83 | 0.7 | 0.72 | 11.869 | 2668.45 | 17.2872 | 3888.36
| 0.75 | 3.5 | 0.875 | 5.25 | 10.2 | 2295 | 22 | 4940 | 139.5 | 31360 | 72.6 | 16310 | 50.8 | 11415 | 0.85 | 0.77 | 0.73 | 8.67 | 1950.75 | 12.3662 | 2776.774
| 0.75 | 6.75 | 0.875 | 8.5 | 19.7 | 4420 | 42.4 | 9525 | 139.5 | 31360 | 72.6 | 16310 | 50.8 | 11415 | 0.77 | 0.69 | 0.77 | 15.169 | 3403.4 | 22.5271 | 5060.6325
HIT-RE
uncracked | 0.5 | 4.5 | 0.75 | 6 | 36.3 | 8155 | 78.2 | 17570 | 59.2 | 13305 | 30.8 | 6920 | 21.6 | 4845 | 0.85 | 0.73 | 0.69 | 30.855 | 6931.75 | 10.8799 | 2440.4265
cracked | 0.5 | 4.5 | 0.75 | 6 | 25.7 | 5780 | 55.4 | 12445 | 59.2 | 13305 | 30.8 | 6920 | 21.6 | 4845 | 0.85 | 0.73 | 0.69 | 21.845 | 4913 | 10.8799 | 2440.4265
cracked | 0.5 | 4.5 | 0.75 | 6 | 25.7 | 5780 | 55.4 | 12445 | 59.2 | 13305 | 30.8 | 6920 | 21.6 | 4845 | 0.58 | 0.73 | 0.69 | 14.906 | 3352.4 | 10.8799 | 2440.4265
14.1992
Updates for v5